## Slide 1: LINAC INTENSITY UPGRADE PHASE II CONTROLS
09/15/2022
Omar Gould

## Slide 2: LINAC INTENSITY UPGRADE PHASE II CONTROLS
09/15/2022
Omar Gould

## Slide 3: AGENDA
Introduction
LINAC Controls Overview
Rationale For Controls Upgrade
Proposed Controls Technology
Timeline
Summary

## Slide 4: Introduction
The Controls Datacon System at the 200 MeV LINAC has been in operation for over five decades.​
Over the years as new accelerator systems have been installed at LINAC, a more modern Controls System has been implemented as an interface.​
The need to significantly expand the capabilities of the LINAC has required a Controls upgrade to meet the new specifications and to maintain reliability.​

## Slide 5: Introduction continued
The 200 MeV LINAC currently has two primary types of Controls for its devices:​
Datacon Systems​
Front End Computer Remote I/O Systems (FRIO)​
A test configuration exist in MOD 2 for two Quad power supplies:​
Quad Function Generator PSI Systems (QFG)​
The Datacon System will be removed completely from
LINAC operations and replaced with two primary Controls
Systems.​

## Slide 6: OVERVIEW
LINAC CONTROLS

## Slide 7: Existing Hardware Controls
The 200 MeV LINAC at BNL currently has two primary types of Controls for its devices:​
Datacon Systems​
Front End Computer Remote I/O Systems (FRIO)​
  VME-4140 Analog Output Module 32 Channels​
  VME-3122 Analog Input Module 32 Channels​
  Existing FRIO systems will remain in operation for the HEBT, BLIP, LEBT and MEBT, Source regions.
Related Exception:​
  Quad Function Generator PSI System for BM1 in HEBT beam line​
​
A Test configuration exist in MOD 2 for 2 Quad power supplies:​
Quad Function Generator PSI Systems (QFG)​
V202 Delay Module​

## Slide 8: Device Types
Vacuum Systems​
  readbacks​
Pulsed Power Supplies​
  Setpoints and readbacks​
  Functions and readbacks​
DC Power Supplies​
  Setpoints and readbacks​
Instrumentation​
  Readbacks​
Sources​
  Setpoints and readbacks​

## Slide 9: RATIONALE
CONTROLS TECHNOLOGY

## Slide 10: RATIONALE
CONTROLS TECHNOLOGY

## Slide 11: Rationale For Controls Upgrade​
Datacon Systems are in operation for over five decades​
  Availability of newer technology​
  Noisy​
  Serial Communication resulting in slower operation as devices are added​
  Obsolete; replacing components is more difficult​
New power supply systems are proposed for the LIUP II ​
  Need to accommodate new power supply specifications​
Ease of expanding Controls​
Performance Improvement​

## Slide 12: PROPOSAL
CONTROLS TECHNOLOGY

## Slide 13: PROPOSAL
CONTROLS TECHNOLOGY

## Slide 14: Proposed Controls
Quad Function Generator PSI Systems (QFG) For Quad PS
V233 Quad Function Generator 4 Channels​
  100 KHz setpoint/readback rate​
  2 to 8 modules per MOD for nine MODs​
PSI 100KHz Power Supply Interface 1 Channel​
  8 to 32 modules per MOD for nine MODs​
V202 Delay Modules 8 Channels​
  1 to 4 modules per MOD for nine MODs​
​
This system will provide noise reduction in addition to meeting and exceeding the specifications of the devices.​

## Slide 15: Software Controls
Existing software will be utilized for interfacing with the upgraded controls.​
  Note Python is replacing Java​
  Reflected Server is no longer utilized​
Presently being used for the upgraded Controls in MOD 2, BM1, and a few other MODs.​
Applications will remain the same for user interfaces with devices.​
ADOs and applications customizations will be implemented as needed.

## Slide 16: Cost: By WBS​ ​

## Slide 17: TIMELINE
CONTROLS IMPLEMENTATION

## Slide 18: TIMELINE
CONTROLS IMPLEMENTATION

## Slide 19: Schedule: Summary ​

## Slide 20: Summary
LINAC CONTROLS UPGRADE

## Slide 21: SUMMARY
LINAC CONTROLS UPGRADE

## Slide 22: SUMMARY
The proposed Controls System is a proven technology currently in use throughout the Collider-Accelerator Facility. Two power supplies in MOD 2 of the 200 MeV LINAC have proven that the QFG System meets and exceeds specifications.​
The noise reduction is significant resulting in improved and reliable performance.​
The proposed Controls System will support LINAC operations for the foreseeable future.​