## Slide 1: CRYOGENICS SYSTEM
ROBERTO THAN

## Slide 2
IR04
56MHZ
STORAGE CAVITY
4.5K

## Slide 3
COOLING TOWER
COMPRESSOR BLDG
REFRIGERATION BLDG
TANK FARM
1006B
LIQUID HELIUM STORAGE
TANK FARM

## Slide 4: SYSTEMS
RHIC STORAGE RINGS 4.5K: FORCED FLOW
IR10: ELECTRON LENSES: 4.5K: BATH
IR02: CEC: SRF CAVITIES: 2K BATH: SUB-ASTMOSPHERIC  HELIUM VACUUM PUMPS
IR02: LEREC: SRF CAVITY: 2K BATH: SUB-ASTMOSPHERIC  HELIUM VACUUM PUMPS
IR04: 56MHZ: 4.5K RE-INSTALL POST RUN22 RUN 24
SPHENIX SOLENOID: 4.5K FINAL INSTALL POST RUN22 RUN 23 -25
AGS COLDSNAKE in AGS Ring

## Slide 5: CRYOGENIC DISTRIBUTION
Service Bld
1006
Service Bld
1010
Service blds
1005H,1005R
Service Bld
1008
Service Bld
1002
Service Bld
1012
ValveBox
ValveBox
ValveBox
ValveBox
ValveBox
ValveBox
ValveBox
ValveBox
ValveBox
IR12
IR2
IR6
IR4
IR10
IR8
CENTRAL PLANT
Service Bld
1004
6 Blue & 6 Yellow Valveboxes
located in service buildings
Cryogenic valves & Recooler,
SC busses current leads interface {“Leadpot”}
C
e
n
t
r
a
l
P
l
a
n
t
R
HS
HR
S
CR
WR
WS
S : Supply, 4.5K Liquid
R : Return, 4.5K vapor Return
H : Heatshield Collider loop
U : Utility, 9.6K Gas Return
M : Magnet, 4.5K Loop
1006
ValveBox
S : Supply, 4.5K Liquid
R : Return, 4.5K vapor Return
H : Heatshield Collider loop
U : Utility, 9.6K Gas Return
WR: Warm Return loop
M : Magnet, 4.5K Loop
1006
ValveBox
S : Supply, 4.5K Liquid
R : Return, 4.5K vapor Return
H : Heatshield Collider loop
U : Utility, 9.6K Gas Return
WR: Warm Return loop
M : Magnet, 4.5K Loop
S : Supply, 4.5K Liquid
R : Return, 4.5K vapor Return
H : Heatshield Collider loop
U : Utility, 9.6K Gas Return
M : Magnet, 4.5K Loop
Sector 5
Sector 4
Sector 3
Sector 2
Sector 1
Sector 12
Sector 11
Sector 10
Sector 9
Sector 8
Sector 7
Sector 6
ValveBox
ValveBox
ValveBox

## Slide 6
125 g/s
85K 9.8bar
45K 14.8bar
HX-3.1
HX-2
HX-1
HX-4
HX-5
HX-6
HX-7.1
HX-3.2
HX-7.2
HX-8.2
HX-8.1
YELLOW RING SHIELD
HX-9
4.45K;1.25bar
473g/s; 4.55K;4.15bar
4.45K;1.25bar
4.65K;1.26bar
1885 g/s;15bar
45 g/s
Current Leads 44 g/s
8.2kW
25kW
54 kW
RHIC Project
HX-20
HX-21
HX-23
HX-24
HX-22
Wcompressor=5.5MW
RHIC 2006 Upgrade
300K
45K
9K
4.5K
CENTRAL PLANT
13 MW COMPRESSOR MOTOR POWER
4/5
4/5
2/3
2/3
12/1
12/1
10/11
10/11
8/9
8/9
6/7
6/7
Maximum 4500 g/s Compressor flow; Original Design Carnot Work: 3.2MW
Equivalent 45kW@4.5K
1  4 bar  16 bar
RHIC: 1800 -2200 g/s
Redundant set of Oil bearing expanders
2x 6 Expander
1 x Gas Bearing expander Expander 7
BLUE RING SHIELD

## Slide 7
EACH MAGNET RING
30 Sextant Recoolers
6 Valvebox Recoolers
TOTAL: 72 Recoolers
472 CORRECTOR MAGNETS LEAD COOLING

## Slide 8: Service building Valveboxes with Leadpot: Magnet Current Leads

## Slide 10
Compressor System 1005H
20 x First Stage Compressors: Howden 321/1.65. 600 HP motor. 235 g/s. + Oil cooler HX
5 x Second Stage Compressors: Howden 321/1.65, 2200 HP. 940 g/s. + Oil cooler HX
Central Intercooler/After cooler Heat exchangers after each compression stage
Oil Coalescers (20 vessels)
Oil vapor removal Charcoal Beds (3 vessel)
Utility Compressor: Howden 255/1.65, 600 HP, 80 g/s
250 g/s Purifier Coldbox system
Oil processing skid
Instrument Air compressor
Maintenance
  Compressor Bearings
  Motor/Compressor Alignments
  Oil Filter cleaning
  Water filter cleaning
  MCC cleaning
  Valves & actuators
  Instrumentation
  Oil change and processing
  Relief devices inspection/recertification
  Charcoal replacement

## Slide 11
Compressor System 1005H
Intercoolers/ Aftercoolers
First Stage Compressor skid
First Stage Compressor Row
2nd Stage
Compressor skid

## Slide 12
Compressor System 1005H: Oil removal
Charcoal Beds
Coalescers
Oil Mist Removal
  4 Stages Coalescers
  5 parallel banks
Oil Processing System
  Vapor removal
  3 parallel charcoal beds
  6 ft diameter
  Oil Vapor Removal
  3 parallel charcoal beds
  6 ft diameter parallel banks

## Slide 13
Compressor System: Purifier
250 g/s
Dual freeze out heat-exchanger
Dual charcoal bed
Regen gas heater
LN2 cooled
Maintenance
  Regeneration
  Valves
  Instruments
  Relief Devices

## Slide 14
4.5K COLDBOX(ES)

## Slide 15
Forced Convection
Ambient vaporizers
Cold Box 4 65-5K
Cold 3 120K-65K
ColdBoxes, last Coldbox 5
65K Charcoal
Adsorption Beds
4.5K Coldbox System

## Slide 16
T1 thru T6 Oil bearing expander + T7 Gas Bearing
Seal Gas Compresssor
Gas Bearing Expander
Rotoflow expander
Oil skid

## Slide 17
LN2 Supply @ 1005H
Twin 6000 Gallons LN2 towers
Gas generation for regeneration
Liquid delivery to Purifier
Liquid N2 Dewars
Maintenance
  Valves
  Relief Devices
  Insulating vacuum
  Defrosting of coils

## Slide 18
Helium Inventory: Gas & Liquid Storage
Maintenance
  Valves
  Relief Devices
  Insulating vacuum
47 Gas Tanks [5,700,000 L]
  ~ 28,000 Liquid Gallons equivalent
3 x 10,000 Gallons [38,000 L] Liquid Helium Dewar
20,000 Gallons [750,000 L] LN2 dewar
Operational Requirement: 48,000 Gallons Liquid helium
Maintenance
  Valves
  Relief Devices
  Insulating vacuum

## Slide 19
Helium Inventory: Gas & Liquid Storage
Liquid Helium Dewars
Liquid N2 Dewar
Tank Farm
Tank Farm

## Slide 20: CRYO CONTROLS
INDEPENDENT CONTROLS FROM MCR
HMI/SCADA: (INDUSOFT) AVEVA EDGE
INTERFACE TO MCS/POWER SUPPLY
  Current leads helium cooling ramps with Magnets current ramping
  Temperature permissive for magnet ramping
  Interlocks for corrector magnets lead cooling
  Interlocks directly to SRF Cavities: 56MHz, CEC, LEREC
  Data cryo to MCR for display

## Slide 21: CRYO CONTROLS
6 SERVICE BUILDINGS:
CRYOCONTROLS PLC RACKS
1005S
MAIN SUPERVISORY SCADA
COMPRESSOR BLDG 1005H
PLC RACKS
REFRIGERATOR BLDG 1005R
PLC RACK

## Slide 22: INTERLOCKS / BEAMPERMIT
Correctors Current leads: NO voltage taps  No quench protection Loss of lead flow  Powers down magnet  BEAM PERMIT
56 MHZ SRF CAVITY @ IP4: Interlock
MAGNET QUENCH  POWER SUPPLY GROUP  QUENCH PROTECTION  BEAM PERMIT
MAGNET POWERING PERMISSIVE
MAGNET TEMPERATURES PERMISSIVE
Oxygen Deficiency Hazard
VODH: VACUUM ODH
Vacuum switches in the magnet cryostats; Triggers ODH alarms
Triggers the cryogenic system sextant valves to close isolating helium inventory
Automatic only active during “ACCESS” MODE

## Slide 25: RHIC EXPERIMENTS WITH CRYOGENICS
COHERENT ELECTRON COOLING
  112MHZ SRF GUN CAVITY @ 4.5K
  704MHZ 5-CELL LINAC@ 2K
Low Energy Rhic Electron Cooling
  704MHZ ½ CELL CAVITY@ 2K
56MHz Storage Cavities
ELECTRON LENSES: 5 T solenoids@ 4.5K
sPHENIX SOLENOID, 1.5 T @4.5K

## Slide 26: COHERENT ELECTRON COOLING

## Slide 27: COHERENT ELECTRON COOLING

## Slide 28: LOW Energy RHIC Electron COOLING

## Slide 29: LOW Energy RHIC Electron COOLING

## Slide 30: ELECTRON LENSES

## Slide 31: ELECTRON LENSES

## Slide 32: 56MHz SRF Cavity

## Slide 33: AGS COLD SNAKE