## Slide 1
Roland Wimmer
BNL
June 30th , 2022
Review of the Gas & Cooling
On Carriage Gas & Cooling Routing

## Slide 2: Detector Cooling Layout
June 30th, 2022
North

## Slide 3: Emcal Cooling Layout
June 30th, 2022
(8) Cooling panels located at each corner on the 1st level, (4) panels for SIPM loop and (4) panels for PreAmp loop
The panels are mounted on a separate frame that will mount to the I-Beams in the corners
Each SIMP panel has (4) 1 ½” supply and (4) 1 ½” return lines. Each one of those lines feed (4) EMCAL sectors
Each PreAmp panel has (4) 2”supply and (4) 2”return lines. Each one of those lines also feeds (4) EMCAL sectors

## Slide 4: Emcal Cooling Layout
June 30th, 2022
Due to the size of the EMCAL cooling lines similar lines will be insulated together to save space
Total vertical width is ~24” and is made up of (7) insulated “bundles”
Example: 4 SIPM Lines insulated together

## Slide 5: TPC Cooling Layout
June 30th, 2022
(4) Cooling panels located at each corner on the 2nd level, mounted on the railings
  The two east panels will also be used for gas
Each panel feeds (2) 1 ½” supply and (2) 1 ½” return lines
The NW panel will be mounted slightly differently to accommodate the altered stairs

## Slide 6: TPOT Cooling Layout
June 30th, 2022
Parasitic to the TPC on the West side
TPOT gets (4) supply and (4) return lines at each end

## Slide 7: INTT Cooling Layout
June 30th, 2022
(2) Detector cooling panels located on the NE & SE corners on the 1st level
The panels will be mounted to the I-Beams on the corners
The south panel feeds (8) 3/8” supply lines and the north panel receives (8) return lines
(2) ECW cooling panels located on the NW & SW corners on the 1st level
Each panel feeds (8) 3/8” supply lines and (8) 3/8” return lines

## Slide 8: MVTX Cooling Layout
June 30th, 2022
(3) Panels located on the east side mid level platform in between the other racks
(72) ¼” Electronic cooling lines from the two 32” panels
(24) ¼” detector cooling lines

## Slide 9: SEPD Cooling Layout
June 30th, 2022
(2) SEPD Connection boxes located under the detector on the east side behind 1E1 & 1E3
Each box feeds (1) ½” supply and (1) ½” return line
Cooling is done via ECW

## Slide 10: Detector Gas Layout
June 30th, 2022

## Slide 11: Main N2 Panel
June 30th, 2022
(2) Main gas panels located at the NE & SE corners of the carriage, outside the pole tip doors
Most gas lines will feed into these panels then out to their destinations
Subsystem | Service | Flow Meters | Lines | Sizes I.D.
EMCAL | N2 | 32 | 32 | 1/4"
INTT | N2 | 2 | 2 | 1/4"
MVTX | N2 (air?) | 1 | 12 | 1/4"
TPC Laser | N2 | 4 | 4 | 1/4"
MBD | Dry Air | 2 | 2 | 1/2"

## Slide 12: EMCAL N2
June 30th, 2022
Located on the 2 main gas panels on the NE & SE corners of the carriage, outside the pole tip doors
(32) ¼” lines on each end

## Slide 13: INTT N2
June 30th, 2022
Located on the 2 main gas panels on the NE & SE corners of the carriage, outside the pole tip doors
(8) ¼” lines on each end

## Slide 14: MVTX N2
June 30th, 2022
Located on the 2 main gas panels on the NE & SE corners of the carriage, outside the pole tip doors
(12) ¼” lines on the south end

## Slide 15: TPC Laser N2
June 30th, 2022
Located on the 2 main gas panels on the NE & SE corners of the carriage, outside the pole tip doors
(4) ¼” lines on each end going to the Laser boxes

## Slide 16: MBD Compressed Air
June 30th, 2022
Located on the 2 main gas panels on the NE & SE corners of the carriage, outside the pole tip doors
(2) ½” lines on each end

## Slide 17: TPC & TPOT Gas Panels
June 30th, 2022
(2) TPC gas panels located at the NE & SE corners of the mid level platform
These panels will be shared between TPC & TPOT cooling and gas
TPC gets (1) line of Ar-CF4 and (1) flow meter at each end
TPOT gets (8) lines of Ar-ISO and (8) flow meters at each end
  (4) supply and (4) return lines at each end

## Slide 18
Any Questions?
June 30th, 2022