## Sheet1
Comment # | DOCUMENT | PAGE | Section | Comment/Issue | Name | BNL Comment/Issue Response | DOE Disposition
1 | USI Evaluation | 2 of 5 | Title | The evaluation and the description must include the fact that while the magnet is cold and measurement and testing is underway, construction activities will continue. | Sullivan | Accepted. Title changed. Additional wording added to executive summary and throughout document.
2 | USI Evaluation Description of Proposed Activity | 4 of 17 | Executive Summary | The dates are not the same as the request letter, please spcecify the correct dates in this document and/or the request letter. | Sullivan | The dates are correct in the USI Evaluation. Due to schedule shifts the ending date of the USI has shifted to 12/7. The letter and the USI have been amended
3 | USI Evaluation Description of Proposed Activity | 5 of 17 | Site, Facilities and Operations Description | Paragraph 5 of this section states the power supply is rated at 5000 amps and 20 volts, is that the correct voltage? If not, please correct in this document. | Sullivan | This is correct. Verified with engineer.
4 | USI Evaluation Description of Proposed Activity | 7 of 17 | Site, Facilities and Operations Description | Task table includes work that is not part of magnet mapping and testing. Potential accident scenarios with each additional task must be included in this USI document and the ODH Analyses. Please add the additional scenarios and analyses or prohibit the additional activities while ODH is present. | Sullivan
5 | USI Evaluation Description of Proposed Activity | 7 of 17 | Safety Analysis | The safety analysis only includes equipment failure scenarios, in order to obtain BHSO approval to include construction work/activities for this USI, all accident scenarios must be analyzed. Please include the analyses as requested or prohibit the additional activities while ODH is present. | Sullivan | (see comment 4)
6 | USI Evaluation Description of Proposed Activity | 9 of 17 | Safety Analysis | Please explain in this document why the Facility Hazard Analysis and Risk Assessment format is used as opposed to the Accelerator Safety Risk Assessment tables. | Sullivan
7 | USI Evaluation Description of Proposed Activity | 10-11 of 17 | ODH Controls | The controls listed in the executive summary indicate that there will be an ODH monitor and alarming system, with operable exhaust ventilation fan and ODH training of all workers in the building. Page 11 indicates that the monitoring system consist of sensors, blue lights, and the purge fan. Please document all appropriate controls in the controls section and be specific (e.g., exhaust rate of fan 27,000 cfm, ceiling fan vs floor fan, generator, sensors etc.). | Cracco | Controls in executive summary are more detailed and consistent with description later in the document.
8 | USI Evaluation Description of Proposed Activity | 11 of 17 | ODH Controls | Paragraph 3, audible and visual alarms must be outside the building also to prevent entry in the event of an ODH event. Please ensure that is in place and described here and other areas of the document as applicable. | Sullivan | There will be visual alarms places at entrances to 1008. Interior audible alarms will be audible form the outside. May need picture showing placement on exterior.
9 | USI Evaluation Description of Proposed Activity | 12 of 17 | ODH Controls | Paragraph 5, this section should state that the supply fan is the redundant backup for the exhaust fan. The supply fan should also be tied to emergency power and should be identified in paragraph 7. Please revise this document to be specific that the required control is 2 fans as part of the ODH system. | Sullivan
10 | USI Evaluation Description of Proposed Activity | 14 of 17 | Appendix I | Please include all analyses for human error/accident scenarios in addition to equipment failure rates. It would be preferable to eliminate all or most of the activities that could introduce these accident scenarios while the ODH is present. | Sullivan | (see comment 4)
11 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | Entire Section | Entire Section | The review of the document’s Appendix 1 entitled Calculation Details for ODH Hazard Evaluation. The appendix contains completed calculations using a Hazard Valuation Tool or HVT, herein known as HVT worksheet(s). These HVT worksheets are located in BSA’s SBMS subject area entitled Oxygen Deficiency Hazards. Dependent on the substance, there are various HVT worksheets the user is directed to complete to classify the oxygen deficiency hazard, i.e., ODH 0, 1, 2 or 3. Based on Appendix 1 in the submittal, CA-D’s ODH classifications were developed using the HVT worksheet for compressed gases and not cryogens. The compressed gas HVT worksheet states “Note: This tool is not applicable for cryogens or liquefied gases such as Carbon Dioxide”. All sheets in the appendix, i.e., pages 16 through 54, used the compressed gas HVT worksheet instead of the cryogen HVT worksheet. | Seniuk | The correct HVT is now used. Note:Both tools give the same answers provided the inventory entered are the same for either the gas form in the compressed gas model tool or liquid form in the cryogen tool.
12 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 1 | Executive Summary | Please explain in this document why it was necessary to include ODH Sensor mitigation only scenarios throughout the analysis. Based on the unmitigated analysis, it was already determined that fans/ventilation are required. | Sullivan
13 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 1 | Executive Summary | Please explain in this document how the ODH system failure rates play into the ODH Class determination and why egress times are needed in these calculations. | Sullivan
14 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 1 | Executive Summary | Please explain in this document why the Fatality rate increases when ventilation is added to the system. | Sullivan
15 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall |  | All | Please revise the document to include ODH calculations for all human error accident scenarios based on the tasks that are planned while the ODH is present. | Sullivan
16 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 5 | 5 | This section states that ODH evaluations are performed with the tools available through SBMS including use of the table, "Failure and Human Error Rates for Probability of Occurrence and the Hazard Evaluation Tool to determine Oxygen Concentrations and ODH Classifications". Please include the actual location of this table and identify where the human error rates were analyzed in this document. | Sullivan
17 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 15 | 7.2 | It appears that ODH Sensor Mitigation only, performs as well as ODH sensor with fan mitigation but it needs to take credit for a 2 minute egress. Where is the 2 minute egress evaluation documented and does it take into account any work obstacles that may be introduced by activities/tasks being performed during the ODH event? Also, does egress time take into acount cognitive and physical delays from an oxygen deficient environment? | Sullivan
18 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 15 | 7.3 | The first bullet in this section is very confusing, how can the O2 sensor and fan/damper failure and working status both be rated at "0"? | Sullivan
19 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 16 | Appendex I | Please provide the institutional Verification and Validation that was performed to certify Hazard Evaluation Tool ODH Calculations software/spreadsheets being used. | Sullivan
20 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 43-52 | Appendex I | Please explain in this document why the O2 concentration at End of Leak with ventilation is still <19.5% and this is considered acceptable. | Sullivan
21 | Calculation of Oxygen Deficiency Hazards for SPHENIX IP8 Hall | 56 | Appendex 4 | Are these tables attempting to demonstrate that the ODH Sensor only with a specific egress time can be used to demonstrate fan/damper mitigation equivalency? Please explain in detail what value these tables add and how egress times were determined in this document. | Sullivan
Note on G90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Goode, George A: Check my response here and see if this makes sense. Reply: @Cirnigliaro, Peter P: Check my response here and see if this makes sense. Reply: I think the comment is questioning the consequences assigned by the table we used...so does our change to align the table with SBMS fix that? Also, aren't there facilities between MIRP facilities and the boundary (depending on which way the wind blows) that are not trained rad workers and spend all day there?
Note on G108: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Goode, George A: Please check my response here... Reply: @Cirnigliaro, Peter P: Please check my response here... Reply: How about: "If the entire water column is lost..." since it's not being removed. The new info in (4) is good, should we add information about the water-level interlocks role in tripping beam if the water falls below the 29.5 ft level?