## Demand Data
Equipment ID | Description | Heat Load kWatts to ECW (estimated) | # of heat exchangers | "Day 1" Demand (gpm) | Check with Pipe Flow model | Temp in (F) | Temp out (F) | Notes
1W1 | EMCAL Digi | 2 | 4 | 8 | x | 68 | 70.3028
1W2 | TPC Laser | 2 | 4 | 8 | x | 68 | 70.3028 | 8 GPM demand assumed at Day 1. Demand/number of heat exchangers to be confirmed by rack building team.
1W3 | EMCAL Digi | 2 | 4 | 8 | x | 68 | 70.3028
2W1 | INTT | 1.5 | 3 | 6 | x | 68 | 70.3028
2W2 | HCAL Control/Digi | 0.85 | 3 | 6 | x | 68 | 69.3049
2W3 | INTT | 1.5 | 3 | 6 | x | 68 | 70.3028
1E1 | EMCAL Digi | 2 | 4 | 8 | x | 68 | 70.3028 | [6 empty] | Level 1 Carriage Rack & Detector Supply
1E2 | Patch Panel | 0.2 | 0 | 0 | x | 68 | #DIV/0! | Correct--Cooling not needed for 1E2 patch panel? |  |  |  | Riser | Branch | Heat Load kWatts | Day 1 Demand gpm | kW |  | GPM
1E3 | EMCAL Digi | 2 | 4 | 8 | x | 68 | 70.3028 |  |  |  |  | West | West Level 1 Racks | 6 | 24 | 52.2 | Racks | 174 | Racks
2E1 | MVTX | 1.1 | 0 | 0 | x | 68 | #DIV/0! | Being cooled sub-atmostpherically by AH Chiller Plant. |  |  |  | West | West Level 1 Detector | 7.2 | 19 | 16.65 | Detector | 39 | Detector
2E2 | HCAL Control/Digi | 0.85 | 3 | 6 | x | 68 | 69.3049 |  |  |  |  | East | East Level 1 Racks | 4.2 | 16 | 68.85 | Total | 213 | Total
2E3 | MVTX | 1.1 | 4 | 8 | x | 68 | 69.2665 | Confirmed 4 Heat exchangers--RP | ECW "Day 1" Loads |  |  | East | East Level 1 Detector | 9.45 | 20
3A1 | EMCAL Digi | 2 | 4 | 8 | x | 68 | 70.3028
3A2 | EMCAL Control/Bias | 1.4 | 3 | 6 | x | 68 | 70.1493 |  | Summary | Heat Load (kW) | Flow Rate (gpm) |  |  | Level 2 Carriage Rack & Detector Supply
3A3 | TPC+TPOT LV | 1.7 | 2 | 4 | x | 68 | 71.9148 | Does +TPOT mean more heat exchangers? No per SB. -- PH | Carriage - Racks | 52.2 | 174 | Riser | Branch | Heat Load kWatts | Day 1 Demand gpm
3A4 | TPC+TPOT LV | 1.7 | 2 | 4 | x | 68 | 71.9148 | Does +TPOT mean more heat exchangers? No per SB. -- PH | Carriage - Detector | 16.65 | 39 | West | West Level 2 Racks | 3.85 | 18
3A5 | EMCAL Control/Bias | 1.4 | 3 | 6 | x | 68 | 70.1493 |  | Chiller Platforms (A&B) | 14.05 | 22 | East | East Level 2 Racks | 3.05 | 14
3A6 | EMCAL Digi | 2 | 4 | 8 | x | 68 | 70.3028 |  | Rack Room - Racks | 20 | 30
3B1 | 24VDC A.Pwr Sys. | 0.5 | 0 | 0 | x | 68 | #DIV/0! | No heat exchanges is correct per SB. -- PH | Rack Room - Portable AC(s) | 0 | 15 |  |  | Level 3 Carriage Rack Supply
3B2 | sEPD | 0.7 | 2 | 4 | x | 68 | 69.612 |  | Total | 102.9 | 280 | Riser | Branch | Heat Load kWatts | Day 1 Demand gpm
3B3 | sEPD | 0.5 | 2 | 4 | x | 68 | 69.1514 |  |  |  |  | East | North Level 3 Racks | 10.2 | 36
3B4 | HCAL LV/Bias | 1.4 | 2 | 4 | x | 68 | 71.2239 | [5 empty] | Mid Level 3 Racks | 14.7 | 30
3B5 | MBD Digitizer | 2 | 3 | 6 | x | 68 | 71.0704 | [5 empty] | South Level 3 Racks | 10.2 | 36
3B6 | MBD Bias | 1 | 2 | 4 | x | 68 | 70.3028 |  |  | 123.48 | 336
3B7 | TPC HV | 8.6 | 4 | 8 | x | 68 | 77.9021 | 8 GPM demand assumed at Day 1. Demand/number of heat exchangers to be confirmed by rack building team. | [5 empty] | Carriage Rack & Detector Supply Totals
3B8 | For future use | 0 | 0 | 0 | x | 68 | #DIV/0! | [5 empty] | Riser | Heat Load kWatts | Day 1 Demand gpm
3B9 | For future use | 0 | 0 | 0 | x | 68 | #DIV/0! | [5 empty] | West | 17.05 | 61
3C1 | EMCAL Digi | 2 | 4 | 8 | x | 68 | 70.3028 | [5 empty] | East | 51.8 | 152
3C2 | EMCAL Control/Bias | 1.4 | 3 | 6 | x | 68 | 70.1493
3C3 | TPC+TPOT LV | 1.7 | 2 | 4 | x | 68 | 71.9148 | Does +TPOT mean more heat exchangers? No per SB. -- PH |  |  |  |  | Total | 68.85 | 213
3C4 | TPC+TPOT LV | 1.7 | 2 | 4 | x | 68 | 71.9148 | Does +TPOT mean more heat exchangers? No per SB. -- PH
3C5 | For future use | 0 | 0 | 0 | x | 68 | #DIV/0!
3C6 | For future use | 0 | 0 | 0 | x | 68 | #DIV/0!
3C7 | For future use | 0 | 0 | 0 | x | 68 | #DIV/0!
3C8 | EMCAL Control/Bias | 1.4 | 3 | 6 | x | 68 | 70.1493
3C9 | EMCAL Digi | 2 | 4 | 8 | x | 68 | 70.3028
Totals for Racks in IR |  | 52.2 | kWatt | 174 |  | gpm
TPC Laser System Box - North | Detector | 0.6 |  | 3 |  | 68 | 69.8422 | Assuming 3 gpm to each box - estimated for 600 watts each
TPC Laser System Box - South | Detector | 0.6 |  | 3 |  | 68 | 69.8422 | Assuming 3 gpm to each box - estimated for 600 watts each
INTT Big Wheel - North | Detector | 1.6 |  | 3 |  | 68 | 72.9127 | 3 gives us a 2 C rise.
INTT Big Wheel - South | Detector | 1.6 |  | 3 |  | 68 | 72.9127 | 3 gives us a 2 C rise.
EMCal pre-amp loop - NE | Detector | 3 |  | 6.5 |  | 68 | 72.2513 | New
EMCal pre-amp loop - NW | Detector | 3 |  | 6.5 |  | 68 | 72.2513 | New
EMCal pre-amp loop - SE | Detector | 3 |  | 6.5 |  | 68 | 72.2513 | New
EMCal pre-amp loop - SW | Detector | 3 |  | 6.5 |  | 68 | 72.2513 | New
sEPD Box - North | Detector | 0.125 |  | 0.5 |  | 68 | 70.3028 | They need about 2 lpm, rounded up
sEPD Box - South | Detector | 0.125 |  | 0.5 |  | 68 | 70.3028
Total for Detectors (IR) |  | 16.65 | kWatts | 39 |  | gpm
AH Plant Chiller #1 (Old) | TPC Chiller | 12 |  | 15 |  | 68 | 75.369 | 15 is max rating of chiller. Actual demand may be less?
AH Plant Chiller #2 (Old) | Running in bypass | 1 |  | 2 |  | 68 | 72.6056 | Demand updated to 1 kW and 2 gpm - 8/10/2022
AH Plant Chiller #3 (old) | Back up |  |  | 0 |  | 68 | #DIV/0! | 15 is max rating of chiller. Actual demand may be less?
AH Sub-Atm 1 | MVTX Sub-atm Det | 0.25 |  | 1 |  | 68 | 70.3028
AH Sub-Atm 2 | MVTX Sub-atm Rack A | 0.4 |  | 2 |  | 68 | 69.8422 | Estimated max
AH Sub-Atm 3 | MVTX Sub-atm Rack B | 0.4 |  | 2 |  | 68 | 69.8422
Chiller Platforms A&B |  | 14.05 | kWatts | 22 |  | gpm
PRR3.1 | Rack Room |  | 0 | 0 |  | 68 | #DIV/0! | ECW lines not connected. Pipes are cut.
PRR3.2 | Rack Room | 6 | 3 | 6 |  | 68 | 77.2112 | Assuming 2 GPM per HX
PRR4.1 | Rack Room | 6 | 4 | 8 |  | 68 | 74.9084 | Assuming 2 GPM per HX
PRR4.2 | Rack Room | 6 | 4 | 8 |  | 68 | 74.9084 | Assuming 2 GPM per HX
Trigger Rack | Rack Room Possible | 2 | 4 | 8 |  | 68 | 70.3028 | Assuming 2 gpm per HX and 4 HXs in this rack. Flow rate demand needs to be confirmed by rack building team.
Rack Room |  | 20 | kWatts | 30 |  | gpm
Portable AC unit | Rack Room | 35 |  | 15 |  | 68 | 89.4929
Rack Room - Portable AC Units |  | 35 | kWatts | 15 |  | gpm
Note on I41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated for power to get a 1 C rise . this is total so 3gpm each side
Note on I42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated for power to get a 1 C rise . this is total so 3gpm each side
Note on I45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I estimate 6 so this is good
Note on I57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Getting load for the other 2 units from the MVTX.