## Slide 1: TPOT Gas and Cooling System
Robert Pisani*
July 20, 2022
*presented by John Haggerty

## Slide 2: Gas System Technical Overview
TPOT Gas System Requirements
  Argon + 5% isobutane : mixture for good gain and stability, slow gas against Lorentz angle
  Module Volume 1.4 liters
  Total Volume 11.2 liters
  Few turns per hour
    50ccm per module (3L/hr)
    400ccm total for whole system
  Slight overpressure above atmosphere (1mBar 0.50”W.C) Max pressure 5mBar
  High purity system
  Single Pass
  Remote monitoring
  Alarmed
West
4 FM North
4 FM South

## Slide 3: The TPOT Gas System
Argon mixture (Ar-Iso) (95-5)
Premix gas bought from vendor
The Pre-Mix gas will not be flammable
There will be no flammable gas in the gas house or IR
Flowrate ~ 400ccm
1-2mBar (~0.5” w.c.) above atmosphere
  to +/- 1/8 w.c.”
Single Pass system
Max pressure 5mBar (bubbler)
Passive over pressure to separate vent (Bubbler)
Supply pressure from Rack ~ 30” W.C.
Return Pressure –Atmosphere
High purity system
  <500 ppm O2
  <100 ppm H2O
PC Monitored (reuse PHENIX TOF.W system)
Alarmed
In IR
Vented at gas house vent stack

## Slide 4: TPOT Gas System Features
Previously Operating PHENIX Gas system (TOF.W)
Basic Features
    Using PHENIX TOF.W controller
    95% Argon + 5% Isobutane (premix)
    Flow controller
    Straight through system
Gas Monitoring
    Monitors system and chamber pressures,
PC controlled and monitored system
    Collects and logs system parameters
    Warnings and Alarms
    Remote monitoring

## Slide 5: TPOT gas lines to IR
South
Tunnel
North
Tunnel
Shield Wall
Gas House
Interaction Region
Existing ¾” copper lines from TOF.W
0.025” W.C. anticipated drop on input lines at 400ccm (50m)
0.025” W.C. drop on return lines
We plan to use 12-pack on the gas pad to minimize the number of bottle changes. 1 bottle will last 3 days, so we would change a 12 pack out every 36 days.
Gas Pad

## Slide 6: Discussion with ESRC
While a component of the gas will be flammable (5% isobutane), when diluted in air to increase the oxygen content to above 12% (the normal oxygen level needed to sustain ignition of a gas), the flammable component goes below the lower flammable limit for isobutane (1.8%).
From the US Bureau of Mines Bulletin 627, it is shown in this chart. It means the blended gas is inert. The safety concern will be ensuring the blend is 95%/5%. If it is purchased from a vendor, it will need QA measures to ensure it is the right mix. If it is blended in house, check precautions will need to be designed into the blending operations to ensure reliable 95%/5% mix.
So, happens I was preparing a document describing protections of physic experiments (passing down the institutional knowledge). I attached a current draft for your info, and feel free to comment.
One item to note, if you use flammable gas detection, it is highly recommended you do not use catalytic bead detection. The technology is subject to poisoning by chemicals, it drifts quickly as it ages and has a poor history of false alarms and high maintenance. IR technology is more expensive but has nowhere near the problems of the catalytic beads.
Sincerely,
Joe [Levesque]
Joe gave us permission to show this. We are now planning on using Pre-Mixed gas from a vendor. The gas in the bottle is not considered flammable

## Slide 7: Gas Summary
The TPOT gas system will used a modified PHENIX TOF.W gas system.
Straight Through system (400ccm)
Premixed gas No flammables.
Passively over-pressure protected.
The system will be alarmed with the ability of remote monitoring and data logging.

## Slide 8: Cooling System
The TPOT cooling system will tap of the already reviewed TPC sub-atmospheric cooling system.
https://indico.bnl.gov/event/10922/
TPOT 320 watts total
8 modules each having 2 TPC Fee Boards
Each Board is 20 watts (high estimate)
Plan to flow 50-100ccm to each module
Total flow 400 to 800ccm.
Temperature monitored on each FEE in several places as well as on cooling manifolds
Power will be interlocked. Flow must be on for power to be turned on. (Hard wired)
Fluid is water with a small part of corrosion / algicide additive ( 10% Opti-Shield+)
Flow Capacity of unit is 300lpm, TPC uses 120lpm and TPOT 1 lpm.
CF-CDU300
Cooling Distribution Unit (CDU)
Negative Pressure Chamber Pump System
Fee hooked up to cooling plated

## Slide 9
Input Cooling Water
Output Cooling Water
Flow set to 100 ccm
In
Out
Temp from Chips
Temp from Chips
Fee 0
Fee 1

## Slide 10
External Chiller required to control temp below 18C. Use current Advantage Chiller M1-5W-SP 5 ton capacity at 10C (17kWatt)
Very Few Flowmeters to reduce restrictions. CDU measures total flow of each loop and monitors for leaks and loads
CF-CDU300, 300 lpm total at 1/2bar (7.25psi) 300kW
-Can supply 75 lpm per loop assuming 7.5 psi pressure drop.
-We will need 28lpm per loop and will see less than 3 psi drop on detector. (confirmed in lab and PipeFlow). This will give a temp rise of about 2C in the coolant
Bypass loops will be added on main trunk lines (not drawn)
14 lpm
14 lpm
28 lpm
14 lpm
14 lpm
28 lpm
Bottom Loop
High Vacuum
(Return)
Lower Vacuum
(Supply)
There are 4 loops
4 channel Unit
2 Feed North
2 Feed South
1
Negative Pressure
System
sPHENIX Electronics Water
15gpm at 85C
Less at 68C
1.5”ID
3/8” ID
30feet
50-100CCM
90 Feet
30 Feet
30 Feet
90 Feet
30 Feet
30 Feet
90 foot1.5” ID
30 foot 1.0”ID
Temp
Pressure Trans
TPOT 1 and 2
Flow
Switch
Supply
1.5”ID
Pressure Trans
Temp
1” ID
Flow
Transmitter
3/8” ID
30feet
50-100CCM
Parflex Polyethylene
Tigerflex® PVC Tubing
1” ID, 30ft

## Slide 11: TPC/TPOT Cooling Panel
TPC
Each Side has 2 loops 2 inputs, 2 outputs,
Each input needs 14
Each Chiller loop has a flow switch to Interlock to LV (Steve’s)
Each Loop has a pressure transmitter
Each Loop has a RTD
Each loop has a return flow transmitter
Temp
Pressure Trans
Dwyer 673-6
1 Chiller Loop
TPOT 1 and 2
To Top A
To Top B
Temp
Pressure Trans
Dwyer 673-6
To Top A
To Top B
Flow
Switch
There will be 4 Sets of the System shown to the left
Loop 1 North Top
Loop 2 North Bottom
Loop 3 South Top
Loop 4 South Bottom
TPOT
TPOT will run parasitic to TPC
2 channels per panel feeds 2 modules
Flow 50-100ccm per module
Power is interlocked with flow switch
Remote monitoring of flow, pressure and temperature
TPOT 1
and 2
Flow
Transmitter
Bypass

## Slide 12
ECW
ECW
=Site Electronics cooling
water 18-20C
1008 Hall
N/S
45ft
E/W
50ft
Interaction area to Mid Labyrinth
Location
of CDU (Cooling Distribution Unit)
40ft
Location
of Chiller
4 panels
One for each chiller loop
At the level of the TPC/TPOT

## Slide 13
Placed so that CDU's reservoir are below the lowest level of the TPC to help with draining
On labyrinth
Secondary Reservoir for draining and filling lines
Using Opti-shield Plus 10% +water
Floor
17ft
12ft
Chiller Platform
7ft
Floor
Beam

## Slide 14
Cooling Summary
The TPOT cooling system uses the TPC cooling system
System parameters are logged and alarmed
Total flow of about 800ccm
Power will be interlocked to flow. Flow must be on to turn on the power.
The system can be monitored remotely.

## Slide 15: Answers to charge questions
Are the interfaces and integration with sPHENIX and RHIC well understood?
  Yes, the gas and cooling systems are accounted for in the sPHENIX interface documents and plans are thoroughly understood by the sPHENIX engineering team.
Is the gas system properly understood, including safety reviews, as needed for operation in sPHENIX?
  Yes, the gas system builds on existing gas infrastructure, and has been presented to the ESRC. Use of premixed gas eliminates the need for flammable gas detection in the IR or Gas Mixing House.

## Slide 16: Backup

## Slide 17
Flowmeters
External Chiller required to control temp below 18C. Use current Advantage Chiller M1-5W-SP 5 ton capacity at 10C (17kWatt)
Very Few Flowmeters to reduce restrictions. CDU measures total flow of each loop and monitors for leaks and loads
Each loop removing 3kWatts
CF-CDU300, 300 lpm total at 1/2bar (7.25psi) 300kW
-Can supply 75 lpm per loop assuming 7.5 psi pressure drop.
-We will need 28lpm per loop and will see less than 3 psi drop on detector. (confirmed in lab and PipeFlow). This will give a temp rise of about 2C in the coolant
Pressure
Transmitter
Bypass loops will be added on main trunk lines (not drawn)
14 lpm
14 lpm
14 lpm
14 lpm
28 lpm
14 lpm
14 lpm
14 lpm
14 lpm
28 lpm
28 lpm
28 lpm
Bottom Loop
Top Loop
High Vacuum
(Return)
Lower Vacuum
(Supply)
This is NORTH
Same for South
4 channel Unit
2 Feed North
2 Feed South
1
2
Negative Pressure
System
sPHENIX Electronics Water
15gpm at 85C
Less at 68C
1.5”ID Tigerflex® WH™ Series Liquid Suction Hose
-20C to 65C,
- 40 PSI rated
-24inHg (Full Vacuum)
-
0.25psi drop over 90 Feet
1” ID
90 Feet
90 Feet
40 Feet
40 Feet
40 Feet
40 Feet
90 Feet
90 Feet
40 Feet
40 Feet
40 Feet
40 Feet
1.0”ID Tigerflex® WH™ Series Liquid Suction Hose
-20C to 65C,
- 45 PSI rated
-24inHg (Full Vacuum)
-
0.20psi drop over 40 Feet
90 foot1.5” ID
40 foot 1.0”ID
Ball Valve 1” ID
Poly Core
FlowSetters
FlowSetters
FROM TPC REVIEW
FROM TPC REVIEW

## Slide 18: Chilldyne
CF-CDU300
We run at 12kWatts- Delta T < 1-2C
120 lpm at 3psi with Temp rise of 2C
On Board Remote monitoring and control.
Use a traditional chiller to control temperature below ECW—See later slide

## Slide 19
Flow set to 50ccm
Input Cooling Water
Output Cooling Water
In
Out
Temp from Chips
Temp from Chips
Fee 0C
Fee 1C

## Slide 20: Setup
9”
60”
70”
In
Out
Flow
100CCM
Delta P is 1.75psi
At 100ccm
1% gauges
30psi F.S.
I have the 2 plates hooked up to a chiller and ready to test. Just have to coordinate with John K to power up and read out temps.

## Slide 21
30 feet .250 ID
30 feet .250 ID
60.5” .125”ID
70” .125”ID
9.5”” .125”ID
20” .061”ID
20” .061”ID
To get 100ccm, a estimated 2.1psi is needed.
Current Tubing to get 100ccm we need 2.1psi.