## Slide 1: Electrical Systems
Jon Sandberg

## Slide 2: Electrical Systems
Electrical Systems Group
(J. Sandberg)
Collider Electrical P.S.
(D. Bruno)
(3 Engineers, 0.5 TS, 12 Technicians
Pulsed Power
(W. Zhang)
(3 Engineers, 0.5 TS, 4 Technicians
Power Distribution
(P.K. Feng)
(2 Engineers , 1 TS)
(R. Lambiase, W. Ng,
C. Schultheiss)
Booster/AGS Ring PS
(I. Marneris)
(3 Engineers, 1 TS, 11 Techs)

## Slide 3: Electrical Systems
The personnel in these groups support the operation, development and upgrades of all C-AD systems. Recent additions including:
          EBIS -184 power supplies
            E Lens-72 power supplies
            OPPIS-PLC controls
Active participation in the Electrical Equipment Inspection Program (EEI)
Active participation in the Electric Materials and Equipment Installation Inspection Program (EMII)
Legacy equipment programs such as removal of obsolete cabling (cable pulling crew) and power distribution equipment
Training for Safety Awareness and use of proper PPE
Concerns and Mitigation of Arc Flash Hazards

## Slide 4: Electrical Systems
~1045 power supplies ranging from 50 Amp bipolar correction supplies to the RHIC Main Dipole and Quadrupole PS’s (5,500 A, 200 V, & 5,500 A, 90 V))
These power supplies can be divided into 15 different types
Superconducting quench detection and protection systems
          309 quench protection assemblies
          36 quench detection systems
          288 crowbar assemblies
          24 DX heater assemblies
Tuning of the quench detection system when significant changes to the operating cycles are
Electrical Testing of the Magnets before and after each Operating Cycle
Major contributor to eLens including the new phase shifting power supply systems (PS and QPA’s). When completed they will be responsible for 34 new power supplies for eLens
To increase system reliability major rebuilds of many hundreds of power supplies has been undertaken successfully over the last decade and a semi-automatic test facility has been built
Maintenance requirements for such a large number of PS is very labor intensive. Changing fans which are near the end of life can take two technicians many months during shutdown periods.
Collider Electrical Power Supply Group (CEPS)

## Slide 5: Electrical Systems
Collider Electrical Power Supply Group (CEPS)
+/- 300 Corrector
RHIC MMPS

## Slide 6: Electrical Systems
Collider Electrical Power Supply Group (CEPS)
450 A, 20 V
100 A

## Slide 7: Electrical Systems
Collider Electrical Power Supply Group (CEPS)
Automatic Test Stand
RHIC MMPS

## Slide 8: Electrical Systems
350 power supplies ranging from 1000 Watt correctors to the 95 MVA AGS main magnet power supply (and associated transformers (8ea) and switchgear)
Four quadrant switch mode supplies (+/- 125 V, +/- 700 A)
Two Quadrant switch mode supplies (+/- 200 V, 1000 A)
SCR supplies (+/- 9,500 V, 5,500 A, AMMPS)
The operation and maintenance of two multi MVA motor generator sets
The Booster main magnet power supply 6,000 V, 6,000 A and associated transformers (30 ea) and switchgear
Electrical testing of the AGS and Booster ring magnets
Maintenance and operations of 79 uninterruptable power supplies
Major contributions to the EBIS (collector supply 15,000 V, 15A), the OPPIS (PLC based control system) and eLense (when complete 44 PS) projects
STAR (1000 V, 5000A) and PHENIX ( 200 V, 3000A) high power PS
Booster/AGS Ring Power Supply Group (BARPS)

## Slide 9: Electrical Systems
Booster/AGS Ring Power Supply Group (BARPS)
AGS MMPS --Transformers, Rectifier Assemblies, and MG Set

## Slide 10: Electrical Systems
Booster/AGS Ring Power Supply Group (BARPS)
Booster MMPS-- Rectifiers, Transformers, and switchgear house

## Slide 11: Electrical Systems
Booster/AGS Ring Power Supply Group (BARPS)
AGS Correctors
Booster Corrector
Tune Quad PS
J10 Dump Bump
BTA PS

## Slide 12: Electrical Systems
Booster/AGS Ring Power Supply Group (BARPS)
BTA PS
Sext PS
Multipole Room PS’s
ETB PS

## Slide 13: Electrical Systems
65 Pulsed power system throughout C-AD
20 systems in the Booster
23 systems in the AGS
20 systems in RHIC
2 in EBIS
Booster Injection kicker 90 V, 1000 A (function 1ms-1.5 ms)
Booster extraction kicker 35,000V, 1,200 A (2,300 ns trapezoidal waveform)
AGS L20 injection septum 350 V, 12,000 A (2 ms, ½ sine waveform)
AGS extraction kickers 35,000 V, 2000 A (360 ns, ½ sine waveform)
RHIC Injection kickers 32,000 V, 1,260 A (160 ns trapezoidal waveform)
RHIC Abort kicker 28,000 V, 21,000 A (22 us irregular waveform)
Cost and delivery of thyratrons is becoming a significant problem. A recent quote for the abort kicker thyratrons is now ~ $40 K. Solid state solution must be found.
4 PS for eLens
Pulsed Power Systems Group (PPS)

## Slide 14: Electrical Systems
RHIC Injection Kicker PS--Controls, Charging Supply and Blumlein pulse generator
Pulsed Power Systems Group (PPS)

## Slide 15: Electrical Systems
RHIC Abort kicker modulators
Pulsed Power Systems Group (PPS)

## Slide 16: Electrical Systems
G10 Modulators
Pulsed Power Systems Group (PPS)
H10 PS

## Slide 17: Electrical Systems
Maintains, Operates, Designs, and Installation of 120/208 V, 480 V, 4160 V, and some limited number of 13.8 kV experimental power distribution systems.
C-AD uses approximately 56 % of the Laboratory power (31 MW)
C-AD utilizes 59 unit substations (13.8 kV / 480 V)
There are two 10 MVA 13.8 kV/ 4,160 V substations which supply power to 26 compressor motors for the RHIC cryogenic system
There are ~8,000 switch and panel boards at C-AD as well as 30,000 molded case circuit breakers
There are 11 diesel generators which supply 2400 kW of emergency power to the complex.
The C-AD Power Distribution Group takes care of low voltage systems (<600 V) for:
          Lighting Systems
          Variable Frequency Drives
          Motor Soft Start Systems
          Automatic transfer switches
          Ground fault detection systems
          Transformers
          Panel boards
          Motor Control Centers (MCC’s)
Power Distribution Group

## Slide 18: Electrical Systems
Responsible for 49, 480 V MCC’s. There is an ongoing effort to replace older MCC’s
In 2006 the C-AD floating Delta system was converted to a high resistance grounded system. Since then remote ground fault detection and monitoring systems have been implemented on 51 substations.
RHIC has 2000 lighting fixtures and 800 lamps and 300 ballasts must be replace annually.
This group has been responsible for 106 work orders (wo’s) so far in 2013, 294 wo’s in 2012, 409 wo’s in 2011, and 336 wo’s in 2010
Replacement of High incident energy switchgear and relays. Since 2006:
        Over 93 beaker settings have been reviewed and optimized
        Soft start circuitry has been added to the STAR main power supply
        45 new solid state trip units have been installed
        New remotely operated switchgear has been installed at 1005 H
        ~ 6000 pieces of equipment have received arc flash labels
        The condition of aging and over-dutied equipment has been brought to forefront and resource are regularly allocated to remediate these conditions
Power Distribution Group

## Slide 19: Electrical Systems
New Transfer switch and load center at Linac reduces arc flash hazard
Power Distribution Group
New Buckets in Linac MCC

## Slide 20: Electrical Systems
Load Center Replacement
Power Distribution Group
Replaced Last Year
Before replacement

## Slide 21: Electrical Systems
912A Emergency Generators
Power Distribution Group
New

## Slide 22: Electrical Systems
1005h, 480 V Main Switchgear replacement now remotely operated
Power Distribution Group

## Slide 23: Electrical Systems
Old 929 MCC
Power Distribution Group
New 929 MCC

## Slide 24: Electrical Systems
New MCC in 928 now under construction
Power Distribution Group

## Slide 25: Electrical Systems
eLens Cable Tray and Wireway
Power Distribution Group

## Slide 26: Electrical Systems
PHENIX Panel Board Replacement
Power Distribution Group
Old
New

## Slide 27: Electrical Systems