## Slide 1: Stave Thermal and Structural FEA/CFD
Preliminary Studies
Stephanie Yang (Oxford)
Adam Huddart (STFC)

## Slide 2
All the results presented are preliminary, numbers and geometry used are first estimates and are not representative of an optimised stave geometry
We are more interested in demonstrating the techniques we intend to use rather than looking too deeply at the results themselves

## Slide 3: L4 Stave Construction

## Slide 4: Material Assignment
Allcomp K9
Duocel Aluminium Foam 8% Relative Density
RVC Carbon Foam
3% Relative Density
0.1 mm carbon fibre
(Optimum layup TBD)
Continuous fibre along central spine
Alice Silicon Sensor
0.1 mm Thick
Kapton FPC 0.1 mm Thick
Ultem end interface w/ O-ring seal

## Slide 5: Material Assignment
Isotropic Elasticity
  Aluminium Foam - Longerons
    101.84 MPa Elastic Modulus
    216.8 kg/m3
  Allcomp K9 - Cross Braces
    650 MPa Elastic Modulus
    200 kg/m3 (known to be quite variable)
  3% RVC Carbon Foam - Centre Spine
    101.84 MPa Elastic Modulus
    45 kg/m3
  Kapton FPC (estimate)
    2.76 GPa Elastic Modulus
    1420 kg/m3
  Silicon (Sensor)
    163 GPa Elastic Modulus
    2329 kg/m3
Orthotropic Properties
  Carbon Fibre Layup
    Young's Modulus
    (CERN/Liverpool data for K13C2U 39% fibre volume)
      X direction – 353 Gpa
      Y Direction – 6 GPa
      Z Direction – 6 Gpa
  2 Layers 0 / +90
    50-micron layer thickness (100 micron total thickness)

## Slide 6: Initial Finite Element Analysis
FPCs (Kapton layer), carbon skin and sensors are geometry modelled as mid plane, with 0.1 mm thick shell elements
Carbon fibre top and bottom plates used layer section to approximate layup

## Slide 7: Modal Simulation
Lowest mode is Y Direction First Harmonic
  108.1 Hz

## Slide 8: Modal Simulation
Second mode is Y Direction Second Harmonic
  279.8 Hz

## Slide 9: Boundary Conditions
Results presented are for a rigidly supported end face
  Removing rigid constraint at one end and allowing for rotation reduces frequencies by approximately 30%
Cone interface/sealing techniques will be important

## Slide 10: Boundary Conditions
Currently two O-rings seal the stave end plate to a inlet support cone
Screws on both end provide a “rigid” mechanical connection
Mechanical connections will need to be tolerant to small variations in stave length and cone separation.

## Slide 11: Thermal FEA Modeling/CFD
2 linked thermal studies
  Effect of heat transfer coefficient
    Examine the temperature profile of a single 5 RSU sensor at various heat transfer coefficient values
    Establish a simplified model with the equivalent power input
  CFD with porous media to test out the input porous parameters
    Use output of heat transfer coefficient model for first estimate of flow parameters of a 3D CFD model

## Slide 12: Sensor FEA geometry
https://indico.cern.ch/event/1341665/contributions/5648416/attachments/2751648/4789826/20231114-WP2-Report.pdf
114.330
Sensor geometry modelled using shell elements.
LEC
RSU
Power density input

## Slide 13: Material properties for thermal and CFD studies
Fluid material name: Air
Solid material_1 name: Silicon
Solid material_2 name: K9 foam

## Slide 14: Power density input
Boundary conditions:
Initial reference T = 22K;
HTC values from 5 to 1000 W/m2C are applied to the whole sensor surface
Steady state thermal analysis
LEC
Pixel matrix
Data backbone
Readout periphery
Biasing

## Slide 15: Thermal FEA result
As expected, the higher the HTC values the smaller the dT.
Chart: h [W/m2C]
| 5 | 100 | 175 | 240 | 300 | 350 | 450 | 550 | 650 | 700 | 1000
Case 1 | 272.53 | 37.704 | 25.664 | 20.504 | 17.428 | 15.545 | 12.849 | 10.995 | 9.631 | 9.075 | 6.764
HTC @ 700 W/m2K

## Slide 16: Simplified sensor model
Applied HTC [W/m^2 K] | Case 1 (detail model) | Case2 (simplified model)
 | dT [C] | dT[C]
5 | 272.53 | 271.37
100 | 37.704 | 37.46
175 | 25.664 | 25.489
240 | 20.504 | 20.36
300 | 17.428 | 17.305
350 | 15.545 | 15.435
450 | 12.849 | 12.758
550 | 10.995 | 10.918
650 | 9.631 | 9.565
700 | 9.075 | 9.012
1000 | 6.764 | 6.72
This result shows that the simplified sensor model with equivalent power input gives the same result as the detail sensor model.
For further CFD studies, the simplified model will be used.

## Slide 17: Simplified sensor model with K9 foams
https://indico.cern.ch/event/1228295/contributions/5390941/
T (ini_ref) = 22C
T_max = 29.53C
Delta T = 7.53C
LEC = 7910W/m2
RSU = 440W/m2
HTC applied to the surfaces of the sensor and K9 foams
K9 foams

## Slide 18: CFD fluid porous 2D test model
Key porous input parameters:
(derived from CERN experiment data: https://indico.cern.ch/event/1228295/contributions/5390941/):
  Porosity: 0.89;
  Inertial resistance factor, C2 =1259.18 [m-1];
  viscous inertial resistance factor, 1/a = 4.12E+08 [m-2]
air

## Slide 19: CFD fluid porous 2D test result
delta T = 7.8K
1000 iterations

## Slide 20: Simple 3D CFD model without foam
Fluid material: Air

## Slide 21: Simple 3D CFD model with foam
Work in progress…..