TSCSW – “The slow controls system will”

## Far Forward Requirements

#### Far Forward Region General Requirements

- TSCSW provide adequate database space to store 12 months of slow controls data on server space within the 1006 building complex.

- TSCSW provide environmental data (ambient temperature, humidity, dewpoint, etc.) to all far forward detectors.

- TSCSW interlock detectors based on collaborator provided fault conditions of the sub-systems monitored by the Slow Controls System.

#### B0PF Detector

- TSCSW monitor the high voltage channels of the B0PF detector at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 100mV.

- TSCSW record the high voltage channels the B0PF detector at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 100mV.

- TSCSW provide use configurable interlock of the B0PF detector based on the high voltage channel rate of change.

- TSCSW monitor the low voltage channels the B0PF detector at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mV.

- TSCSW record the low voltage channels the B0PF detector at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mV.

- TSCSW provide a user configurable interlock of the B0PF detector based on the low voltage channel rate of change.

- TSCSW monitor and record the temperature of the B0PF detector at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

#### B0 Crystal Calorimeter

- TSCSW monitor the temperature of the B0 SiPMs at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

- TSCSW record the temperature of the B0 SiPMs at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 0.1°C.

- TSCSW monitor the high voltage channels at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mV.

- TSCSW record the high voltage channels at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 10mV.

- TSCSW monitor the leakage current of the B0 SiPMs at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mA.

- TSCSW record the leakage current of the B0 SiPMs at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 10mA.

- TSCSW provide an interface to the B0 calorimeter cooling system.

#### Roman Pots & Off Momentum Detector (OMD) Requirements

- TSCSW provide a motion control interface and positional feedback system for the OMD.

- TSCSW prevent detector insertion past a maximum insertion value to prevent damage to the detectors.

- TSCSW relay the beam position within the beam to the detector by way of the EIC main control room.

- TSCSW monitor the supplied voltage to the Roman Pots and OMD at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mV.

- TSCSW record the supplied voltage to the Roman Pots and OMD at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 10mV.

- TSCSW monitor the temperature of the Roman Pots and OMD at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

- TSCSW record the temperature of the Roman Pots and OMD at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 0.1°C.

#### ZDC Requirements

- TSCSW monitor the temperature of the ZDC SiPMs at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

- TSCSW record the temperature of the ZDC SiPMs at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 0.1°C.

- TSCSW monitor the high voltage channels of the ZDC SiPMs at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mV.

- TSCSW record the high voltage channels of the ZDC SiPMs at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 10mV.

- TSCSW monitor the leakage current of the ZDC SiPMs at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mA.

- TSCSW record the leakage current of the ZDC SiPMs at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 10mA.

- TSCSW provide an interface to the ZDC HCAL calibration system.

## Far Backward Requirements (Ken)

#### Far Forward Region General Requirements

- TSCSW provide adequate database space to store 12 months of slow controls data on server space within the 1006 building complex.

- TSCSW provide environmental data (ambient temperature, humidity, dewpoint, etc.) to all far backward detectors.

- TSCSW interlock detectors based on collaborator provided fault conditions of the sub-systems monitored by the Slow Controls System.

#### Low Q2 Tagger – Trackers (Ken)

- TSCSW provide an interface for managing the parameters of all the Timepix4 ASICs.

- TSCSW monitor the temperature of the Timepix4 ASICS at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

- TSCSW record the temperature of the Timepix4 ASICS at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 0.1°C.

- TSCSW monitor the Low voltage and current supplied to the Low Q2 Taggers at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mV / 10mA.

- TSCSW record the Low voltage and current  supplied to the Low Q2 Taggers at a user settable rate on a scale from 0.3mHz to 17mHz with a precision of 10mV / 10mA.

- TSCSW provide a motion control interface and positional feedback system for the Low Q2 Taggers.

- TSCSW provide an interface to the Low Q2 Tagger cooling system.

- TSCSW monitor the temperature of the Low Q2 Taggers cooling water at user settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

- TSCSW record the temperature of the Low Q2 Taggers’ cooling water at user settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

- TSCSW monitor the leakage current on the Bias supply of the Timepix4 Si sensors at a user settable rate on a scale from 0.3mHz to 1Hz with a precision to be determined.

- TSCSW record the leakage current on the Bias supply of the Timepix4 Si sensors at a user settable rate on a scale from 0.3mHz to 17Hz with a precision to be determined.

- TSCSW monitor the  Bias voltage of the Timepix4 Si sensors at a user settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mV.

- TSCSW record the  Bias voltage of the Timepix4 Si sensors at a user settable rate on a scale from 0.3mHz to 17Hz with a precision of 10mV.

#### Low Q2 Tagger – Calorimeter (Jarda)

- SCSW …...

#### Lumi Calorimeter – (Krzysztof)

- SCSW …...

#### Lumi Pair Spectrometer Trackers (Nick)

- SCSW …...

#### Lumi Pair Spectrometer - Calorimeters (Nick)

- TSCSW monitor the temperature of the Calorimeter SiPMs at a user-settable rate on a scale from 0.3mHz to 17mHz with a precision of 0.1°C.

- TSCSW record the temperature of the Calorimeter SiPMs at a user-settable rate on a scale from 0.3mHz to 17mHz with a precision of 0.1°C.

- TSCSW monitor the high voltage channels of the SiPMs at a user-settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mV.

- TSCSW record the high voltage channels of the SiPMs at a user-settable rate on a scale from 0.3mHz to 17mHz with a precision of 10mV.

- TSCSW monitor the leakage current of the SiPMs at a user-settable rate on a scale from 0.3mHz to 1Hz with a precision of 10mA.

- TSCSW record the leakage current of the SiPMs at a user-settable rate on a scale from 0.3mHz to 17mHz with a precision of 10mA.

- TSCSW provide a motion control interface and positional feedback system for the calibration collimator.

- TSCSW provide a motion control interface and positional feedback system for the converter (multiple foils/Empty)

- TSCSW monitor the temperature of the Converter at a user-settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

- TSCSW record the temperature of the Converter at a user-settable rate on a scale from 0.3mHz to 1Hz with a precision of 0.1°C.

- LED System controls

- Converter Colling system controls (flow/liquid temp)

- Control for Dipole Magnet Current / Field measurement