## Slide 1
RRPL Operations
RRPL - Week of 09/30:
  Production
    LANL Th target processing this week
    Ni/Co Hot Cell set-up in TPL; preparation for BLIP irradiated foil processing
  F&O:
      rooftop unit replacement work October 10 – job walkdown
      reheat coils developed leak: 9/29 – on schedule to have relocation of conduit on Wednesday 10/1 and work on the weekend to follow
    Coming weeks:
      Ac-225 dispensing to customers

## Slide 2
BLIP Operation – OFF Season Mode
  Chillers require 24-hr for crankcase heater warmup prior to operation. Therefore, cannot immediately switch to backup chiller until installation of electrical panel is performed in the next phase of cooling system upgrade.
  Off-season maintenance/testing:
      Scheduling chillers 1 + 2 Preventative Maintenance for the week of October 6.
      This week weekly alarms testing.
      Differential filter pressure alarm issue, meet with water group SME to discuss.

## Slide 3
  Commissioning Path Forward: Commissioning has restarted.
    Access controls recertification completed 9/26. We are now out of ACS USI and working under module 2 of the commissioning plan.
    Ion Source testing – replacement filament power supply installed and tested 9/5. Ion source is running but at lower current than desired. PEEK tubing replacement fixed arcing issue. Bias supply tested up to 25Kv, still issue with low current 9/22
    RF is operational. RF survey conducted 9/29 per module 2 of the commissioning plan. USI for new access controls ‘testing/tuning modes’ – approved by RSC, forwarded to LESHC
    New robot - robot testing/programming in progress in vault room when access allows.
  Low-current beam test today 9/30 or tomorrow, awaiting ESR and RWP to begin first foils irradiation
  RF tube sparking issue 9/22, tube repaired and tested successfully.
  New chipmunk installed in control room due to multiple false alarms, MCR received 2 more alarms on 9/24 on new unit . C- AD group informed, awaiting reply.
  Bench testing helium cooling recirculation system 9/30.
Cyclotron Activities