## Slide 1: Detector Cooling - Update
Girish Gowda

## Slide 2: Forward EMCAL
Sectional View
Temperature Requirements
Maintain FEB temperature 3 C above dew point
Cooling the SiPMs to be determined

## Slide 3: Forward EMCAL
Sector Geometry
Exploded View
Copper tube (inch)
0.25
FEB
SiPM
Acrylic
Epoxy
Tungsten Scifi
Heat Sink
Thermal Pad
Copper tube
SiPM Board

## Slide 4: Forward EMCAL – CFD Simulation
Water flow rate (litre/min) | Flow velocity (m/s) | Tube Length (m) | Pressure drop (psi) | Temperature rise (C) | FEB Heat load (W) | SiPM Heat load (W)
0.83 | 0.76 | 6 | 2.1 | 2 | 4.5 | 0.17
CFD Data :
Technical Data :
Water flow rate (litre/min) | Flow velocity (m/s) | Tube Length (m) | Pressure drop (psi) | Temperature rise (C) | Half FEB Heat load (W) | SiPM Heat load (W)
0.83 | 0.76 | 0.21 | 0.07 | 0.04 | 2.25 | 0.17
Materials
Copper thickness (10 %) in FEB
Copper thickness (5%) in SiPM Board
FEB and SiPM Board thickness : 2 mm

## Slide 5: Forward EMCAL – CFD Simulation
SiPM Temperature
FEB Temperature
Ambient Temperature (C) | Flow velocity (m/s) | Half FEB Heat load (W) | SiPM Heat load (W)
20 | 0.76 | 2.25 | 0.17
Relative Humidity (%) | Dew Point Temperature (C) | Water Inlet Temperature (C) | FEB Temperature (C) | SiPM Temperature (C)
100 | 20 | 22 | 25.9 | 23.8
Heat Sink Temperature

## Slide 6: Forward EMCAL – CFD Simulation – Scenario 1
Relative Humidity :
SiPM Temperature
FEB Temperature
Ambient Temperature (C) | Flow velocity (m/s) | Half FEB Heat load (W) | SiPM Heat load (W)
20 | 0.76 | 2.25 | 0.17
Relative Humidity (%) | Dew Point Temperature (C) | Water Inlet Temperature (C) | FEB Temperature (C) | SiPM Temperature (C)
100 | 20 | 22 | 25.9 | 23.8
60 | 12 | 14 | 20.22 | 22.85

## Slide 7: Forward EMCAL – CFD Simulation – Scenario 2
Heat Transfer Coefficient :
Ambient Temperature (C) | Flow velocity (m/s) | Half FEB Heat load (W) | SiPM Heat load (W)
20 | 0.76 | 2.25 | 0.17
Heat Transfer Coefficient (W/m^2 C) | Dew Point Temperature (C) | Water Inlet Temperature (C) | FEB Temperature (C) | SiPM Temperature
5 | 20 | 22 | 25.9 | 23.8
1 | 20 | 22 | 27.51 | 28.19
FEB Temperature
SiPM Temperature

## Slide 8: Forward EMCAL – CFD Simulation – Scenario 3
Velocity :
Ambient Temperature (C) | Flow velocity (m/s) | FEB Heat load (W) | SiPM Heat load (W)
20 | 0.76 | 4.5 | 0.17
Velocity (m/s) | Dew Point Temperature (C) | Water Inlet Temperature (C) | FEB Temperature (C) | SiPM Temperature (C)
0.76 | 20 | 22 | 25.9 | 23.8
2 | 20 | 22 | 25.64 | 23.75
FEB Temperature
SiPM Temperature

## Slide 9: Forward EMCAL – CFD Simulation
Design :
SiPM Temperature
FEB
SiPM Board
FEB
SiPM Board
SiPM Temperature

## Slide 10: Summary
Suggestions :
Modifying geometry from straight tube to serpentine tube will enhance heat transfer and reduce FEB temperature further.
Adding fins or turbulators in heat sink will enhance heat transfer and aid in cooling of FEB.
SiPM boards integrated with FEB heat sink downstream with thermal pad aids in improved cooling on SiPM’s,