## Slide 1: Detector Cooling - Update
Girish Gowda
05/05/2025

## Slide 2: Forward EMCAL
Sectional View
Temperature Requirements
Forced Convection Cooling for FEB’s with and without comparison
Cooling the SiPMs to be determined

## Slide 3: Forward EMCAL - Scenario 1
Sector Geometry
Exploded View
FEB
SiPM
Acrylic
Epoxy
Tungsten Scifi
SiPM Board

## Slide 4: Forward EMCAL – CFD Simulation - Scenario 1
FEB Heat load (W) | SiPM Heat load (W)
4.5 | 0.17
CFD Data :
Technical Data :
Half FEB Heat load (W) | SiPM Heat load (W)
2.25 | 0.17
Materials
Copper thickness (10 %) in FEB
Copper thickness (5%) in SiPM Board
FEB and SiPM Board thickness : 2 mm
Simulation
Copper tubes, heat sink & thermal pad geometry not considered

## Slide 5: Forward EMCAL – CFD Simulation - Scenario 1
SiPM Temperature
FEB Temperature
Ambient Temperature (C) | Half FEB Heat load (W) | SiPM Heat load (W)
20 | 2.25 | 0.17
Heat Transfer Coefficient (W/m^2 C) | FEB Temperature (C) | SiPM Temperature (C)
5 | 48.0 | 24.1

## Slide 6: Forward EMCAL – CFD Simulation – Scenario 1
Heat Transfer Coefficient :
Ambient Temperature (C) | Half FEB Heat load (W) | SiPM Heat load (W)
20 | 2.25 | 0.17
Heat Transfer Coefficient (W/m^2 C) | FEB Temperature (C) | SiPM Temperature (C)
1 | 143.8 | 30.8
FEB Temperature
SiPM Temperature

## Slide 7: Forward EMCAL - Scenario 2
Sector Geometry
Exploded View
Copper tube (inch)
0.25
FEB
SiPM
Acrylic
Epoxy
Tungsten Scifi
Heat Sink
Thermal Pad
Copper tube
SiPM Board

## Slide 8: Forward EMCAL – CFD Simulation - Scenario 2
Water flow rate (litre/min) | Flow velocity (m/s) | Tube Length (m) | Pressure drop (psi) | Temperature rise (C) | FEB Heat load (W) | SiPM Heat load (W)
0.83 | 0.76 | 6 | 2.1 | 2 | 4.5 | 0.17
CFD Data :
Technical Data :
Water flow rate (litre/min) | Flow velocity (m/s) | Tube Length (m) | Pressure drop (psi) | Temperature rise (C) | Half FEB Heat load (W) | SiPM Heat load (W)
0.83 | 0.76 | 0.21 | 0.07 | 0.04 | 2.25 | 0.17
Materials
Copper thickness (10 %) in FEB
Copper thickness (5%) in SiPM Board
FEB and SiPM Board thickness : 2 mm
Simulation
Copper tubes, heat sink & thermal pad geometry considered

## Slide 9: Forward EMCAL – CFD Simulation - Scenario 2
SiPM Temperature
FEB Temperature
Ambient Temperature (C) | Flow velocity (m/s) | Half FEB Heat load (W) | SiPM Heat load (W)
20 | 0.76 | 2.25 | 0.17
Heat Transfer Coefficient (W/m^2 C) | Water Inlet Temperature (C) | FEB Temperature (C) | SiPM Temperature (C)
5 | 22 | 25.9 | 23.8
Heat Sink Temperature

## Slide 10: Forward EMCAL – CFD Simulation – Scenario 2
Heat Transfer Coefficient :
Ambient Temperature (C) | Flow velocity (m/s) | Half FEB Heat load (W) | SiPM Heat load (W)
20 | 0.76 | 2.25 | 0.17
Heat Transfer Coefficient (W/m^2 C) | Water Inlet Temperature (C) | FEB Temperature (C) | SiPM Temperature (C)
1 | 22 | 27.51 | 28.19
FEB Temperature
SiPM Temperature

## Slide 11: Summary
Observations :
Modifying geometry without consideration of copper tubes, heat sink & thermal pad drastically increases temperature in FEB deprived of forced convection cooling as shown in slide 7.
Temperatures of FEB are further aggravated with natural convection cooling deprived due to lower heat transfer coefficient in addition to forced convection cooling as shown in slide 6.
Modifying geometry from straight tube to serpentine tube will enhance heat transfer and reduce FEB temperature further.
Adding fins or turbulators in heat sink will enhance heat transfer and aid in cooling of FEB.
Suggestions :