## Slide 1: sPhenix Quench Detector Review
March 15, 2017

## Slide 2: Overall Description
Superconducting Magnet with 25 Voltage Taps
  Additional 4 Redundant Taps
Energy Dump Resistor
Quench Detector
Strain Gage and Temperature Sensors System

## Slide 3: Requirements
The system will be powered by a UPS.
The system will have a watch dog timer.
  The PXIe quench signal out will be a square wave that will be toggled every time the software completes a loop.
    The signal will also be used to time the duration of a loop.
  When a quench is detected the signal will go low, and stay low.
  This signal will go to a board that will implement the watch dog timer and output the interlock quench signal.
    The interlock quench signal will normally be high.
    This board will look for transitions; if the transitions stop the board will lower the interlock quench signal.
Capability of real-time display of raw and processed data, on demand.
The system will have test points to monitor the measured parameters in real time.
The system will provide the ability to time-correlate the samples.
  The Quench Detector will record the time of each event.
  The fast and slow loggers will include the quench event signal to help time-correlate the samples.

## Slide 4: Requirements Continued
The Quench detector will have 24 channels (3 PXIe-4300 Boards).
  Channels are listed in the Excel file.
  Gains are listed in the Excel file. Assumptions are:
    The maximum ramp rate is 3.125 A/sec.
    The A/D will have 16 bits resolution for +/- 10 V input.
  The system will sample at 720 Hz.
    The system should have simultaneous sampling on all channels.
    The sample clock will be from a PLL locked to the power line.
      This same PLL will supply the clock for the fast logger.
  It will have a hardware anti-aliasing filter.
    8th order.
    corner frequency of 85 Hz.
  It will have a software integrator.
    Integrate 12 samples, this puts notches at integer multiples of 60 Hz.
    No decimation.
  The system will implement three algorithms.
    Vmeas – (L * di/dt.)
    Vhalf coil comparison.
      Half coils are not identical, may need a scaling factor between them.
    For the gas-cooled leads and flex leads a fixed threshold.
  The system will trigger if any algorithm detects a quench.
  The internal signals will be sent to circular buffers that stores 20 seconds of data (14400 samples/channel; 576 kBytes total storage).
    The circular buffer will have 10,800 pre-trigger data points (3/4 buffer pre-trigger).
    Graphs of the buffers should be available after a quench.
The system will have an adjustable time delay for each algorithm.

## Slide 5: Requirements Contimued
The fast logger will implement a circular buffer on 32 channels.
  Sample Rate of 2880 Hz (4*720 Hz).
    The sample clock will be from a PLL locked to the power line.
  Gain of the analog section will be
  Separate anti-aliasing filters from the Quench Detector.
    8th order
    Corner frequency of 340 Hz.
  It will store 10 seconds of data per channel (28,800 samples/channel; 1.152 Mbytes total storage).
    The circular buffer will have 21,600 pre-trigger data points (3/4 buffer pre-trigger)
  The circular buffers will stop on a quench signal.
  Graphs of the buffers should be available after a quench.
The slow logger will store all 32 channels continuously.
  Sample Rate of 1 Hz.
  It will decimate the data from the fast logger.
    ? stage CIC anti-aliasing filter.
  Graphs of the buffers should always be available.

## Slide 6: Quench Detection Algorithms
The system will implement three algorithms.
    Vmeas – (L * di/dt.)
    Vhalf coil comparison.
      Half coils are not identical, may need a scaling factor between them.
    For the gas-cooled leads and flex leads a fixed threshold.
After Rotator failure in 2009 the half coil comparison was done on different Rotator magnets with the same current.

## Slide 7: Signal Processing Block Diagram

## Slide 8: Ramp Frequency Content

## Slide 9: Differentiator Frequency Response

## Slide 10: Percent Errors of Different Differentiator Methods

## Slide 11: Anti-Aliasing Filter Frequency Response

## Slide 12: Anti-Aliasing Filter Circuit

## Slide 13: Integrator Frequency Response

## Slide 14: Total Frequency Response

## Slide 15: Front-End Electronics
Copy RHIC Quench Detector Front End
  Use RHIC Quench Detector Front End up to AD210BN
  Anti-Aliasing Filter will be new design
Voltage Clamp
  Designed for 300 V, exponential decay with a time constant of 39.5 seconds. (L/R = 2.57 H / 65 mOhm)
  Use current limiting resistors in magnet as part of circuit
Open Lead Detection
  REF200 Current Source and balancing resistors
Isolation
  Provided by AD210BN
    DC continuous 3500 Vpeak
Gains
  Gain of 10 for superconducting busses
  Gain of 1 for magnet coils, gas-cooled leads, flex bus

## Slide 16: RHIC Front-End Electronics

## Slide 17: Voltage Taps

## Slide 18: Voltage Taps continued

## Slide 19: Voltage Taps continued

## Slide 20: Quench Detector Channel Assignments

## Slide 21: Interlocks
Cryo interlock
  Cryo system is ready and at temperature
Gas-Cooled Lead Flow interlock
  Gas-Cooled Lead Flow is appropriate for the Current
Quench System Interlock
  Quench System is running and not in a quench state
Quench Contactor Interlock
  Quench Switch is closed

## Slide 22: Interlocks continued
POWER SUPPLY INTERLOCKS AND SIGNALS
Water Flow Interlock
  ADDED FLOW SWITCH INTLK
SCR Fuse Interlock
  NO SCR FUSE INTERLOCK – ALL BUSS UNIT
SCR Over-Temperature Interlock
  ADDED KLIXON TO EACH SCR 12 EACH PLUS CROWBAR SCR
Transformer Temperature Interlock
  Rectifier 1
  Rectifier 2
  Interphase
  ADDED KLIXONS TO MAIN TXFM – NOT INTERPHASE TFMR

## Slide 23: Interlocks continued
Cabinet Temperature Interlock
  ADDED CUBICLE OT DEVICE
Control Power Interlock
  CONTROL POWER HAS 10A BREAKERS IN FRONT OF PS
AC Input Under-Voltage
  AC PHASE LOSS ONLY
AC Input Over-Current
  AC CURRENT IMBALANCE RELAY
AC Sequence Interlock
  AC SEQUENSE INTERLOCK BUILT IN TO REGULATOR BUCKET
DC Output Over-Voltage
  NO PROTECTION
DC Output Over-Current
  DC OVER CURRENT INTERLOCK BY FRONT PANEL METER TO PLC
Output Ripple Interlock
  NO PROTECTION
Output Filter Fuse Interlock
  OUTPUT FILTER FUSE AND TRIGGER INT TO PLC

## Slide 24: Interlocks continued
Enclosure Door Interlock
  FRONT AND REAR DOOR INT TO PLC
ADDED WATER LEAK DETECTION
  INT TO PLC
GROUND FAULT
  INT TO PLC
DCCT FAULT
  INT TO PLC
ADDED WATER SOLENOID
  CONTROL BY PLC
ADDED REAR DOOR FANS AND AIR VAINS
  AIR VAINS ARE WARNING NOT INT
DUMP RESISTOR AND CONTACTOR
  CONTACTOR LOCAL / REMOTE CONTROLS
  CONTACTOR AUXILIARY CONTACTS
  PS DCCT SIGNAL
  RESISTOR GROUND OPTION