## Sheet1
ePIC SVT Air Supply Plant - Requirements
Contact |  |  |  | Color key:
| Joe Silber <jhsilber@lbl.gov> |  |  | INPUT
| Lawrence Berkeley National Laboratory |  |  | CALCULATED
LINKED
Version history
v1 - 2025-11-11 - JHS - initial version
v2 - 2025-11-19 - JHS - wider T_stability, diverter, moisture in terms of DPs, possible enclosure, add'l comments
v3 - 2026-03-19 - JHS - state volumetric flow in SCFM
Abstract
The Silicon Vertex Tracker (SVT) is a key subsystem of the Electron-Proton/Ion Collider (ePIC) detector. It will probe the smallest internal building blocks of visible matter -- quarks and gluons -- and help us understand the underlying laws that govern the strongest force in nature. The SVT is composed of thousands of custom silicon sensors. They will be cooled by a steady supply of cleaned, conditioned, cooled air. This specification is for the plant which will generate that cooling air. This specification does not include the transmission of that air to the SVT.
ID | Category | Description | Name | Value (SI) | Units (SI) | Value (US) | Units (US) | Comments
0 | process air | temperature - nominal | T_nom | 3 | °C | 37.4 | °F | Possible future relaxation of T_nom to +12°C (TBD)
1 | output air | temperature - adjustment range - min | T_min | -5 | °C | 23 | °F | Possible future relaxation of T_min to +7°C (TBD)
2 | output air | temperature - adjustment range - max | T_max | 30 | °C | 86 | °F
3 | output air | temperature - stability about setpoint | T_stability | ±2 | °C | ±3.6 | °F
4 | output air | pressure dew point - max allowable | PDP_max_allow | -10 | °C | 14 | °F | Pressure dew point shall never exceed this value when output stream is flowing through the process outlet. Possible future relaxation of PDP_max_allow to +3°C (TBD).
5 | output air | pressure dew point - stability | PDP_stability | ±2 | °C | ±3.6 | °F
6 | output air | pressure dew point - setpoint adjustment | PDP setpoint | Pressure dew point shall be settable within a range defined by the AQ_water class (at low end) to PDP_max_allow (at high end).
7 | output air | pressure - nominal | P_nom | 0.44 | bar (gauge) | 6.38 | psi (gauge)
8 | output air | pressure - adjustment range - min | P_min | 0.03 | bar (gauge) | 0.435 | psi (gauge)
9 | output air | pressure - adjustment range - max | P_max | 0.75 | bar (gauge) | 10.875 | psi (gauge)
10 | output air | pressure - stability about setpoint | P_stability | ±0.02 | bar (gauge) | ±0.29 | psi (gauge)
11 | output air | mass flow rate - nominal | ṁ_nom | 1 | kg/s | 132 | lbm/min
12 | output air | mass flow rate - adjustment range - min | ṁ_min | 0.1 | kg/s | 13.2 | lbm/min
13 | output air | mass flow rate - adjustment range - max | ṁ_max | 1.5 | kg/s | 198 | lbm/min
14 | output air | volumetric flow rate - nominal | V_nom | 2941.1765 | Sm³/hr | 1731.1111 | SCFM | stated at standard air conditions, not at true air density of plant output
15 | output air | volumetric flow rate - min | V_min | 294.1176 | Sm³/hr | 173.1111 | SCFM | stated at standard air conditions, not at true air density of plant output
16 | output air | volumetric flow rate - max | V_max | 4411.7647 | Sm³/hr | 2596.6667 | SCFM | stated at standard air conditions, not at true air density of plant output
17 | output air | air quality - solid particulate | AQ_particulates | Class 1 | per ISO 8573-1:2010 |  | -
18 | output air | air quality - total oil | AQ_oil | Class 1 | per ISO 8573-1:2010 |  | - | Oil-free compression or high-end filtration is critical to prevent oil contamination
19 | output air | air quality - humidity / water | AQ_water | ≤ Class 3 | per ISO 8573-1:2010 |  | - | Class 2 PDP = -40°C, Class 3 = -20°C, might consider Class 4 (PDP=+3°C) if significant cost savings and if T_min could be increased to ~ +10°C (TBD)
20 | output air | output diverter | diverter_valve | Plant shall have an integrated 3-way diverter valve on the output stream. Outlets are to "process" (goes to SVT instrument) and "bypass" (exhaust). Fail-safe state (e.g. upon loss of power) shall be to the bypass outlet.
21 | facility | hose inner diameter - process air | Dh_process | 100 | mm | 4 | in | Connects to the SVT
22 | facility | hose inner diameter - bypass air | Dh_bypass | TBD | mm | TBD | in | Connects to facility exhaust
23 | facility | hose fitting type - process air | fitting_process | TBD | - | - | -
24 | facility | hose fitting type - bypass air | fitting_bypass | TBD | - | - | -
25 | facility | electrical - plug form | e_plug | TBD | - | - | -
26 | facility | supply voltage | V_supply | TBD | - | - | -
27 | facility | supply frequency | f_supply | 60 | Hz | - | -
28 | facility | heat rejection - coolant | coolant | TBD | - | - | -
29 | facility | heat rejection - coolant temperature | Tc | TBD | °C |  | K
30 | facility | heat rejection - coolant flow rate limit | Vc | TBD | L/min |  | ?
31 | facility | heat rejection - coolant pressure | Pc | TBD | ? |  | ?
32 | environment | ambient temperature during operation - avg | T_amb_avg | 23 | °C | 73.4 | °F | Based on 15 year STAR WAH data 99.73% (3σ) envelope
33 | environment | ambient temperature during operation - min | T_amb_min | 18 | °C | 64.4 | °F | Based on 15 year STAR WAH data 99.73% (3σ) envelope
34 | environment | ambient temperature during operation - max | T_amb_max | 32 | °C | 89.6 | °F | Based on 15 year STAR WAH data 99.73% (3σ) envelope
35 | environment | ambient dewpoint during operation - avg | DP_amb_avg | 5.2 | °C | 41.36 | °F | Based on 15 year STAR WAH data 99.994% (4σ) envelope
36 | environment | ambient dewpoint during operation - max | DP_amb_max | 22.1 | °C | 71.78 | °F | Based on 15 year STAR WAH data 99.994% (4σ) envelope
37 | control | fault condition on process air | process_fault | System shall have a process_fault condition, based on measured state of the output air. The state is logically TRUE when any of the key parameters (temperature, pressure, or pressure dew point) falls outside either its user-configured allowable range or the limit values listed here (whichever is more restrictive).
38 | control | output diverter control | diverter_ctrl | System shall automatically direct output air to the bypass outlet during startup, shutdown, or process_fault state.
39 | control | control interface - local | ctrl_local | Plant shall have a local user-interface panel by which it can be operated.
40 | control | control interface - remote | ctrl_remote | Plant shall have an API allowing customer to integrate it into our facility's control system, for configuring, monitoring, and real-time control.
41 | control | emergency shut-off - local | shutoff_local | Emergency shut-off shall be readily achievable by pressing an easily-identifiable hardware button, by any person physically stationed near the plant.
42 | control | emergency shut-off - remote | shutoff_remote | Emergency shut-off shall be readily achievable by a simple electrical interlock signal.
43 | maintenance | uptime during normal operations | uptime | 99.5 | %
44 | package | max width | W_max | TBD | m | TBD | in
45 | package | max length | L_max | TBD | m | TBD | in
46 | package | max height | H_max | TBD | m | TBD | in
47 | package | max weight | M_max | TBD | kg | TBD | lbm
48 | package | enclosure | enclosure | TBD, possibly enclose loud components (e.g. compressor) for moderate sound dampening.