## Sheet1
Cooling Air Flow Stages |  |  | Color key:
Contact: jhsilber@lbl.gov |  |  | INPUT
CALCULATED
Version history |  |  | LINKED
v1 - Jun 24, 2025 - JHS - initial version
v2 - Jun 27, 2025 - JHS - fixed corrugation area calc
v3 - Jun 30, 2025 - JHS - fixed factor 1/2 in ΔP₂₃ₙ calc
v4 - Jul 15, 2025 - JHS - 5 stages, cross-section totals
v5 - Sep 08, 2025 - JHS - 6 stages, named, including exhaust stage
v6 - Oct 21, 2025 - JHS - disk and barrel stave geometry details
v7 - Oct 21, 2025 - JHS - added module power loads
v8 - Oct 22, 2025 - JHS - add FPC power, update loads to "max" estimates, alt sensor + power counts sheet, RSU len --> 21.6 mm
v9 - Oct 23, 2025 - JHS - correct downstream T₂ and T₃ with KE terms
v10 - Oct 27, 2025 - JHS - define downstream pressure BC by a desired positive internal ambient pressure within SVT volume; nozzle vs orifice selection
v11 - Oct 30, 2025 - JHS - fix bar defn, fix rect section hydraulic diam, add flow restrictor / nozzle stages
v12 - Oct 31, 2025 - JHS - fix sign error in ΔP₂₃ₙ, remove superfluous extra "nozzle" stage, add note on restrictor neg pressure
v13 - Nov 04, 2025 - JHS - separate stages for restrictor/manfold, distinguish expansion pressure model from contraction, add energy balance checks
v14 - Nov 11, 2025 - JHS - quantize and define supply pipes, calculate insulation thickness to prevent condensation in hot/wet exterior conditions
v15 - Dec 18, 2025 - JHS - assume Aerogel insulation; update L3 stave count to 44
v16 - Feb 17, 2026 - JHS - reduce hot/wet conditions (assume HVAC interlock) from DP 22C to 15C; finer-graining on iterative insulation thickness calc
v17 - Mar 19, 2026 - JHS - narrow and widen exhaust duct geometry as needed for CAD design; add additional pressure drop for stave internals; add calculation of SCFM flowrate; add initials in rev hist
v18 - Apr 22, 2026 - JHS - set air supply RH to 1% (approx -40C DP), and nominal internal positive pressure at 0.001 bar
v19 - May 05, 2026 - JHS - make supply dewpoint more clearly be the driving input for SVT interior dewpoint; set blower-oriented boundary conditions (9°C @ channel/stave inlets)
Physical constants and unit conversions
standard pressure (air) | P_std | Pa | 101325
standard temperature (air) | T_std | K | 288.71
standard density (air) | ρ_std = P_std / (R * T_std) | kg/m³ | 1.2228
standard dynamic viscosity (air) | μ_std | Pa*s | 1.81e-05
zero celsius | T₀ | K | 273.15
specific gas constant (air) | R | J/(kg*K) | 287
heat capacity ratio (dry air @ 20C) | γ | - | 1.4
specific heat capacity (dry air @ 20C) | cₚ = R γ / (γ - 1) | J/(kg*K) | 1004.5
isentropic temperature exponent | k = (γ-1)/γ | - | 0.28571
critical pressure ratio (choked flow) | βₓ = Pₓ / P = [2/(γ+1)]^[1/k] | - | 0.52828
sudden contraction pressure loss coefficient | κ_contract | - | 0.42 | empirical approx value
infinity | ∞ | - | 1e+99
cfm per m³/s | cfm_per_m3s | - | 2118.88
Pa per bar | Pa_per_bar | - | 100000
in H₂0 per bar | inH20_per_bar | - | 401.463
psi per bar | psi_per_bar | - | 14.5038
bar per atm | bar_per_atm | - | 1.0132
Insulation properties, boundary conditions, and assumptions
insulation material thermal conductivity | k_insul | W/(m*K) | 0.02 | <-- 0.05 for typical insulation wraps, ATLAS uses silica aerogel ~ 0.02 W/(m*K)
" | " | US R-value @ 1" | 7.2118
insulation thickness design factor | t_design_factor | - | 1.5
typical convection coefficient outside insulation | h_insul | W/(m² * K) | 5
exterior hot/wet dew point | Td_humid | °C | 13 | 286.15 | K | 22.1 C = 4σ (99.994% envelope) value in WAH data 2010-2025 13.2 C = max value in sPHENIX hall data 2024 for 4 months
exterior hot/wet temperature | Tamb_humid | °C | 20 | 293.15 | K | 35 C = corresponding ambient temperature in WAH data 2010-2025 20 C = corresponding ambient temperature in sPHENIX hall data 2024 for 4 months
SVT interior average air temperature | Tamb_svt | °C | 18.6577 | 291.8077 | K | from calculations below
air supply relative humidity | RH_supply | % | 80%
air supply dewpoint calc intermediate term | γ_supply = ln(RH_supply * exp((17.62 * Tₛ) / (243.12 + Tₛ))) | - | 0.26998
air supply dewpoint | Td_supply = (243.12 * γ) / (17.62 - γ) | °C | 3.7831 | 276.9331 | K
SVT interior dew point | Td_svt = Td_supply | °C | 3.7831 | 276.9331 | K | assuming 100% displacement of by supply (i.e. supply input >> moist air back flow or effusion from outside ambient)
Disk geometry
corrugation pitch | xc | mm | 34.7
corrugation height | hc | mm | 6
corrugation cross-sectional area | Ac ~ xc * hc / 2 | mm² | 104.1
corrugation hydraulic diameter | Dc = √(4 Ac / π) | mm | 11.5128
large disk diameter (D1-D4) | Dd14 | mm | 870
small disk diameter (D0) | Dd0 | mm | 488
num large disks (per side) | nd14 | - | 4
num small disks (per side) | nd0 | - | 1
avg disk diameter (areally weighted) | Dd = √((Dd14²*nd14+Dd0²*nd0)/(nd14+nd0)) | mm | 808.1762
avg large disk corrugation length | Lc14 ~ π / 4 * Dd14 | mm | 683.2964
avg small disk corrugation length | Lc0 ~ π / 4 * Dd0 | mm | 383.2743
avg corrugation length | Lc ~ π / 4 * Dd | mm | 634.7401
avg num corrugations (per half disk) | ncd ~ (Dd/2) / (xc/2) | - | 23.2904 | <-- non-integer is ok, it's averaging large and small disks
Layers geometry
stave channel width (this is one side) | ws | mm | 20.65
stave channel height at edge | hs1 | mm | 2.92
stave channel height at center | hs2 | mm | 7.49
stave channel avg height | hs = (hs1 + hs2)/2 | mm | 5.205
stave channel cross-sectional area | As ~ ws * hs | mm² | 107.4832
stave channel hydraulic diameter | Ds = √(4 As / π) | mm | 11.6984
variation from disk corrug hydraulic diameter | Ds / Dc - 1 | - | 1.612% | <-- this is pretty similar to disk corrugation hydraulic diameter
L4 stave length | Ls4 | mm | 793
L3 stave length | Ls3 | mm | 503
num L4 staves (per top/bottom half) | ns4 | - | 35
num L3 staves (per top/bottom half) | ns3 | - | 22
avg stave channel length | Ls = (Ls4*ns4+Ls3*ns3)/(ns4+ns3) | mm | 681.0702
variation from disk corrug avg length | Ls / Lc - 1 | - | 7.299% | <-- this is pretty similar to disk average corrugation length
Note: given geometric similarity of average barrel staves to average disk corrugation channels, I treat them all as basically the same in flow calcs below.
num half disks equivalent to an OB half | nds_equiv = Ls * (ns4 + ns3) / (Lc * nc) |  | 2.626 | <-- non-integer is ok, it's averaging lots of things
Disk and layer air supply quantizations
num pipes half disks | npd |  | 5
num pipes per quarter L4 | np4 |  | 2
num pipes per quarter L3 | np3 |  | 1
avg num channels per pipe | nc = ncd * (npd + nds_equiv) / (npd + np4 + np3) |  | 22.2015 | <-- non-integer is ok, it's averaging disks and layers
SVT internal volume geometry
approx percent of internal volume which is ambient air | vf_amb | - | 90%
PST diameter | D_pst | mm | 1076
PST length | L_pst | mm | 2540
SVT total internal ambient air volume | v_svt = vf_amb * π/4 * D_pst² * L_pst | mm³ | 2078694419
number of internal ambient air subvolumes | nᵥ | - | 12 | <-- 6x between large disks, 2x between D4 and MPGD disks, 2x small disk + IB, 1x outside L4, 1x between L3/L4
average SVT internal subvolume's volume | vᵥₐ = v_svt / nᵥ | mm³ | 173224534.9
num subvolumes between large disks | nᵥₗ | - | 6
typical gap between large disks | gᵥₗ | mm | 423.2012
rough equiv hydraulic diameter between large disks | Dᵥₗ = √(4 / π * D_pst * gᵥₗ) | mm | 761.4381
L4 diameter | D_L4 | mm | 840
L3 diameter | D_L3 | mm | 540
rough equiv hydraulic diameter outside L4 | Dh_L4 = √(D_pst² - D_L4²) | mm | 672.4403
rough equiv hydraulic diameter between L3/L4 | Dh_L34 = √(D_L4² - D_L3²) | mm | 643.4283
average SVT internal subvolume's hydraulic diameter | Dᵥₐ = (nᵥₗ * Dᵥₗ + D_L3 + Dh_L34 + Dh_L4) / (nᵥₗ + 3) | mm | 713.8331
average SVT internal subvolume's length | Lᵥₐ = vᵥₐ / (π/4 * Dᵥₐ²) | mm | 432.8388
Exhaust duct geometry
exhaust duct width | wₑₓ | mm | 35
exhaust duct height | hₑₓ | mm | 104
exhaust duct cross-sectional area | Aₑₓ = wₑₓ * hₑₓ | mm² | 3640
exhaust duct perimeter | Pₑₓ = 2 * (wₑₓ + hₑₓ) | mm | 278
exhaust duct hydraulic diameter | Dₑₓ = 4 Aₑₓ / Pₑₓ | mm | 52.3741
number of exhaust ducts per internal ambient subvolume | nₑₓ | - | 1
Module power loads
reference link for power loads | Copy of EIC-LAS Power - 2025-10-22 | Also see adjoining sheet where RSUs are counted in an alternate way.
power per LEC | Q_1lec | W | 0.208
power per RSU | Q_1rsu | W | 0.208
typical num RSU per module | n_rsu_per_mod | - | 5.6519 | <-- average, calculated on adjoining sheet
typical EIC-LAS power | Q_eiclas = n_rsu_per_mod * Q_1rsu + Q_1lec | W | 1.3836
AncASIC power multiple of EIC-LAS | qf_aa | - | 45%
typical power per AncASIC | Q_1aa = qf_aa * Q_eiclas | W | 0.62262
FPC power multiple of EIC-LAS | qf_fpc | - | 30%
typical power per FPC | Q_1fpc = qf_fpc * Q_eiclas | W | 0.41508
length per RSU | L_rsu | mm | 21.6
num rsu per avg corrug length (exact coverage) | n_rsu = Lc / L_rsu | - | 29.3861 | <-- non-integer is ok, it's averaging stuff
num modules per avg corrug length | n_mod = n_rsu / n_rsu_per_mod | - | 5.1993
total RSU power per avg corrug | Qc_rsu = Q_1rsu * n_rsu | W | 6.1123
total LEC power per avg corrug | Qc_lec = Q_1lec * n_mod | W | 1.0815
total AncASIC power per avg corrug | Qc_aa = Q_1aa * n_mod | W | 3.2372
total FPC power per avg corrug | Qc_fpc = Q_1fpc * n_mod | W | 2.1581
total power per avg corrug | Qc = Qc_rsu + Qc_lec + Qc_aa + Qc_fpc | W | 12.5891
total power per avg module | Q_mod = Qc / n_mod | W | 2.4213 | <-- cross-check this against others' current-best-estimates
total modules modeled below | n_mod_system = L₄ * N₄ * n_mod | - | 3693.8346 | <-- cross-check this against others' current-best-estimates
Stave/channel impedances
L4 single stave pressure drop (abs value) | ΔPz_s4 | bar | 0.02 | 2000 | Pa | Giovanni Rizzo CFD Oct 2025 --> ~20 mbar for L4 staves ... https://docs.google.com/presentation/d/1Gv-qn9MdSMsqow9QPCXmvO5Zp7N3LvAs/edit?slide=id.p6#slide=id.p6
Large disk single corrugation pressure drop (abs value) | ΔPz_d1 | bar | 0.003 | 300 | Pa | Jaime Cruz-Duran FEA Dec 2025 --> ~3 mbar for large disk corrugations ... https://docs.google.com/presentation/d/1QkX378p579N6oKIsQGXBjSSW25JkBPqp/edit?slide=id.p24#slide=id.p24
Generic channel pressure drop | ΔPz = max(ΔPz_s4, ΔPz_d1, ...) | bar | 0.02 | 2000 | Pa | assume we regulate subdetectors that have lower impedances up to match the highest
Boundary conditions
source temperature | Tₛ | °C | 7 | 280.15 | K | <-- in practice, we would control a heater on the input airstream outside the detector until T₁ below is as desired
source pressure | Pₛ | bar | 1.4266 | 0.41339 | bar (gauge) | Iteratively solved, so always check carefully for reasonability, and that final outlet pressure = Pₑ boundary condition. If it misbehaves, the usual move is (1) Copy the formula. (2) Type in a numeric value that's a decent initial guess. (3) Paste the formula back in.
" | " | Pa | 142664.1776 | 41339.1776 | Pa (gauge) |  | 2 | bar, source pressure iterative solver initial guess
" | " | psi | 20.6917 | 5.9958 | psi (gauge)
source mass flow rate | ṁₛ | kg/s | 0.95
source volume flow rate (standard air conditions) | Vₛ = ṁₛ / ρ_std | m³/s | 0.77687 | 1646.1033 | SCFM
SVT internal ambient volume's positive pressurization | ΔP₊ | bar (gauge) | 0.001 | 0.40146 | in H₂0 (gauge) | must be >= 0 bar. This is really just a nominal value that shifts Pᵦ, reminding us that we will have/need *some* small positive pressurization
SVT internal ambient volume's pressure | Pᵦ = P_std + ΔP₊ | bar | 1.0143 | 1.001 | atm | must be >= 1 atm
Each "stage" consists first of a length of pipe with a friction factor, then a change of cross-sectional area |  |  | It's not trivial to insert or remove column channels in this spreadsheet.
1 = entrance = at beginning of stage |  |  | To calculate fewer than 6 distinct channels:
2 = downstream = after pipe length, but before area change |  |  | - set "nᵢ" to 1 for the dummy channel(s), i.e. no splitting of parent
3 = outlet = manifold = after area change |  |  | - set L, D_mm, and hs to same value as their respective parents
stage description | - | - | source --> ePIC | branches to hadron + electron sides | branches to top + bottom halves | pipes into ePIC to half disks and half barrels | pipes within SVT to half disks and half barrels | manifold | disk channels and staves | SVT internal ambient volumes | exhaust ducts
stage index | - | - | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
num channels (per parent channel) | nᵢ | - | 1 | 2 | 2 | 8 | 1 | 1 | 22.2015 | 0.016891 | 1 | <-- values > 1 are splits, less than 1 are mergers
total num channels in system | Nᵢ = product(nᵢ) | m | 1 | 2 | 4 | 32 | 32 | 32 | 710.4495 | 12 | 12
mass flow per channel | ṁ = (ṁₛ or previous stage ṁ) / nᵢ | kg/s | 0.95 | 0.475 | 0.2375 | 0.029687 | 0.029687 | 0.029687 | 0.0013372 | 0.079167 | 0.079167 | 0.95 | kg [check-product], mass flow is split exactly among branches at each stage, i.e. assuming each branch has similar back-pressure
length | L | m | 10 | 10 | 15 | 7 | 3 | 0.1 | 0.63474 | 0.43284 | 10
hydraulic diameter (mm) | D_mm | mm | 100 | 75 | 50 | 23 | 23 | 23 | 11.5128 | 713.8331 | 52.3741 | <-- for supply, up to ~ 3"-4" pressure-rated hose is probably practical; ducts could be larger if pressure kept below about 1 bar
hydraulic diameter | D | m | 0.1 | 0.075 | 0.05 | 0.023 | 0.023 | 0.023 | 0.011513 | 0.71383 | 0.052374
single channel cross-sectional area along length L | A₁₂ = π D² / 4 | m² | 0.007854 | 0.0044179 | 0.0019635 | 0.00041548 | 0.00041548 | 0.00041548 | 0.0001041 | 0.40021 | 0.0021544
all channels total cross-sectional area | ΣA₁₂ = A₁₂,ᵢ * Nᵢ | m² | 0.007854 | 0.0088357 | 0.007854 | 0.013295 | 0.013295 | 0.013295 | 0.073958 | 4.8025 | 0.025853
" | " | cm² | 78.5398 | 88.3573 | 78.5398 | 132.9522 | 132.9522 | 132.9522 | 739.5779 | 48024.6746 | 258.526
entrance temperature | T₁ = Tₛ or previous stage T₃ | K | 280.15 | 280.5294 | 279.773 | 281.2324 | 281.0062 | 280.8784 | 282.3814 | 291.8077 | 291.3437
" | " | °C | 7 | 7.3794 | 6.623 | 8.0824 | 7.8562 | 7.7284 | 9.2314 | 18.6577 | 18.1937 | <-- aim for desired temperature at corrugation or stave inlet (see highlighted cell)
entrance pressure | P₁ = Pₛ or previous stage P₃ | Pa | 142664.1776 | 138974.1685 | 132253.085 | 117310.3172 | 107627.3194 | 103108.4389 | 103540.7685 | 101425.0003 | 100636.4905
" | " | bar | 1.4266 | 1.3897 | 1.3225 | 1.1731 | 1.0763 | 1.0311 | 1.0354 | 1.0143 | 1.0064
entrance density (ideal gas law) | ρ₁ = P₁ / (R * T₁) | kg/m³ | 1.7744 | 1.7261 | 1.6471 | 1.4534 | 1.3345 | 1.2791 | 1.2776 | 1.2111 | 1.2036
entrance dynamic viscosity | μ₁ = μ₀ * (T₁/T₀)^0.76 | Pa*s | 1.7691e-05 | 1.7709e-05 | 1.7673e-05 | 1.7743e-05 | 1.7732e-05 | 1.7726e-05 | 1.7798e-05 | 1.8247e-05 | 1.8225e-05
Reynold's number | Re = 4 ṁ / (π D μ₁) | - | 683737.2816 | 455356.2317 | 342218.6525 | 92627.2228 | 92683.8884 | 92715.9425 | 8309.159 | 7738.4625 | 105599.0503
friction factor (Blasius) | f = 64/Re, Re < 2300 = 0.316/Re^0.25 otherwise | - | 0.010989 | 0.012165 | 0.013065 | 0.018114 | 0.018111 | 0.018109 | 0.033098 | 0.033692 | 0.01753
friction pressure drop (Darcy-Weisbach) | ΔP₁₂ = -f * (L/D) * ṁ² / (2 ρ₁ A₁₂²) | Pa | -4530.6426 | -5431.2104 | -17408.1183 | -9682.9978 | -4518.8805 | -157.1458 | -117.8336 | -0.00033005 | -1877.5703
additional idiosyncractic internal impedance | ΔPz₁₂ | Pa | 0 | 0 | 0 | 0 | 0 | 0 | -2000 | 0 | 0 | to capture details like internal restrictions within a stave
downstream pressure | P₂ = P₁ + ΔP₁₂ + ΔPz₁₂ | Pa | 138133.535 | 133542.958 | 114844.9667 | 107627.3194 | 103108.4389 | 102951.2931 | 101422.9349 | 101425 | 98758.9202
" | " | bar | 1.3813 | 1.3354 | 1.1484 | 1.0763 | 1.0311 | 1.0295 | 1.0142 | 1.0143 | 0.98759
ambient pressure in the downstream area of this stage | P_local_ambient | bar | 1.0132 | 1.0132 | 1.0132 | 1.0143 | 1.0143 | 1.0143 | 1.0143 | 1.0143 | 1.0132
downstream pressure relative to local ambient | description(P₂ - P_local_ambient) | - | positive | positive | positive | positive | positive | positive | approx neutral | approx neutral | relative vacuum | For case with flow restrictors, note how negative pressure arises in this region. All plumbing in this zone would need to be well-sealed and leak-tight to prevent ingress of ambient air.
module power input to stream | Q = Qc * Nᵢ if channel or stave else 0 | W | 0 | 0 | 0 | 0 | 0 | 0 | 8943.9116 | 0 | 0 | <-- note total applied power, cross-check with others' current-best-estimates
stream temperature rise due to external heat input | ΔTq₁₂ = Q / (Nᵢ * ṁ * cₚ) | K | 0 | 0 | 0 | 0 | 0 | 0 | 9.3725 | 0 | 0
entrance air speed | u₁ = ṁ / (ρ₁ * A₁₂) | m/s | 68.1697 | 62.2884 | 73.4371 | 49.1631 | 53.5431 | 55.8643 | 10.0542 | 0.16334 | 30.5317
approx downstream density (for kinetic energy calc) | ρ₂~ = P₂ / (R * T₁) | kg/m³ | 1.718 | 1.6587 | 1.4303 | 1.3334 | 1.2785 | 1.2771 | 1.2515 | 1.2111 | 1.1811
approx downstream air speed (for kinetic energy calc) | u₂~ = ṁ / (ρ₂~ * A₁₂) | m/s | 70.4056 | 64.8217 | 84.5687 | 53.5862 | 55.8897 | 55.9495 | 10.2641 | 0.16334 | 31.1122
kinetic energy term | ΔTk₁₂ = (u₁² - u₂~²) / (2 * cₚ) | K | -0.15423 | -0.16028 | -0.87548 | -0.22622 | -0.12782 | -0.0047459 | -0.0021233 | 0 | -0.017811 | <-- accounts for net effect of friction and acceleration; u₂ is solved iteratively from coupled P₂, T₂, ρ₂; P₂ (calculated by Darcy-Weisbach) carries the friction term
downstream temperature | T₂ = T₁ + ΔTq₁₂ + ΔTk₁₂ | K | 279.9958 | 280.3691 | 278.8976 | 281.0062 | 280.8784 | 280.8736 | 291.7518 | 291.8077 | 291.3259
" | " | °C | 6.8458 | 7.2191 | 5.7476 | 7.8562 | 7.7284 | 7.7236 | 18.6018 | 18.6577 | 18.1759
downstream density (ideal gas law) | ρ₂ = P₂ / (R * T₂) | kg/m³ | 1.719 | 1.6596 | 1.4348 | 1.3345 | 1.2791 | 1.2771 | 1.2113 | 1.2111 | 1.1812
downstream air speed | u₂ = ṁ / (ρ₂ * A₁₂) | m/s | 70.3668 | 64.7847 | 84.304 | 53.5431 | 55.8643 | 55.9486 | 10.6047 | 0.16334 | 31.1103
average density | ρₐ = (ρ₁ + ρ₂)/2 | kg/m³ | 1.7467 | 1.6929 | 1.5409 | 1.394 | 1.3068 | 1.2781 | 1.2444 | 1.2111 | 1.1924
average volumetric flow | Vₐ = ṁ / ρₐ | m³/s | 0.54389 | 0.28059 | 0.15413 | 0.021297 | 0.022718 | 0.023228 | 0.0010745 | 0.06537 | 0.066394
" | " | cfm | 1152.4478 | 594.5314 | 326.5767 | 45.1261 | 48.1363 | 49.2168 | 2.2768 | 138.5104 | 140.6818
total volumetric flow (all channels) | ΣVₐ = Vₐ * Nᵢ | m³/s | 0.54389 | 0.56118 | 0.61651 | 0.68151 | 0.72697 | 0.74329 | 0.7634 | 0.78444 | 0.79673
" | " | cfm | 1152.4478 | 1189.0629 | 1306.307 | 1444.0354 | 1540.3621 | 1574.9376 | 1617.5534 | 1662.1248 | 1688.1818 | <-- note how first column gives volume flow rate reqt at source density, while last column (if vacuum is applied to exhaust) gives req't on vacuum pump (at assumed density)
average air speed | uₐ = Vₐ / A₁₂ | m/s | 69.2508 | 63.512 | 78.4963 | 51.2597 | 54.679 | 55.9064 | 10.3221 | 0.16334 | 30.8183 | <-- aim for desired airspeed within corrugation in the highlighted cell
cross-sectional area on other side of outlet | A₃ = ∞ or next stage's (A₁₂ * n) | m² | 0.0088357 | 0.003927 | 0.0033238 | 0.00041548 | 0.00041548 | 0.0023112 | 0.0067598 | 0.0021544 | 1e+99
area change pressure drop (non-choked) | ΔP₂₃ₙ = ṁ²/(2*ρ₂) * (1/A₁₂² - 1/A₃²) | Pa | 893.173 | -925.1081 | 3319.348 | 0 | 0 | 1934.2855 | 68.0935 | -557.4806 | 571.6014 | <-- Bernoulli, lossless
outlet pressure if non-choked | P₃ₙ = P₂ + ΔP₂₃ₙ | Pa | 139026.708 | 132617.8499 | 118164.3146 | 107627.3194 | 103108.4389 | 104885.5786 | 101491.0284 | 100867.5194 | 99330.5216 | <-- preferable case (non-choked)
outlet pressure if choked | P₃ₓ = P₂ * βₓ | Pa | 72973.4308 | 70548.3126 | 60670.5043 | 56857.5527 | 54470.3104 | 54387.2932 | 53579.8893 | 53580.9803 | 52172.5389 | <-- probably don't want a sonically choked design, but the possibility is calculated here for completeness
pressure ratio calculated with non-choked eqn | β₃ₙ = P₃ₙ / P₂ | - | 1.0065 | 0.99307 | 1.0289 | 1 | 1 | 1.0188 | 1.0007 | 0.9945 | 1.0058 | <-- more tolerant designs will have outlet:inlet pressure ratios well above 0.528 (sonic)
is choked? | β₃ₙ < βₓ | boolean | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
approx outlet pressure | P₃~ = P₃ₙ or P₃ₓ | Pa | 139026.708 | 132617.8499 | 118164.3146 | 107627.3194 | 103108.4389 | 104885.5786 | 101491.0284 | 100867.5194 | 99330.5216
approx outlet air speed (incompressible) | u₃~ = u₂ * A₁₂ / A₃ | m/s | 62.5483 | 72.8828 | 49.8015 | 53.5431 | 55.8643 | 10.0577 | 0.16331 | 30.3426 | 0
approx outlet temperature | T₃~ = T₂ + (u₂² - u₃~²) / (2 * cₚ) | K | 280.513 | 279.8142 | 281.2007 | 281.0062 | 280.8784 | 282.3814 | 291.8077 | 291.3495 | 291.8077
approx outlet density | ρ₃~ = P₃~ / (R * T₃~) | kg/m³ | 1.7269 | 1.6514 | 1.4642 | 1.3345 | 1.2791 | 1.2942 | 1.2119 | 1.2063 | 1.1861
expands at outlet? | A₃ > A₁₂ | boolean | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE
sudden contraction loss coefficient | K ~ 0.42 * (1 - (A₃ / A₁₂)²) | - | n/a | 0.088148 | n/a | 0 | 0 | n/a | n/a | 0.41999 | n/a
outlet pressure, Bernoulli contraction with loss | P₃_contract = P₂ + (ρ₂*u₂² - (1+ K)*ρ₃~*u₃~²) / 2 | Pa | n/a | 132253.085 | n/a | 107627.3194 | 103108.4389 | n/a | n/a | 100636.4905 | n/a
outlet pressure, Borda-Carnot expansion | P₃_expand = P₂ + ṁ * (u₂ - u₃~) / A₃ | Pa | 138974.1685 | 132563.4318 | 117310.3172 | 107627.3194 | 103108.4389 | 103540.7685 | 101425.0003 | 100316.0088 | 98758.9202 | <-- Borda-Carnot expansion, empirical, lossy, momentum conservation with assumption P₂ applies at area A₃
outlet pressure | P₃ = select between contract, expand | Pa | 138974.1685 | 132253.085 | 117310.3172 | 107627.3194 | 103108.4389 | 103540.7685 | 101425.0003 | 100636.4905 | 98758.9202
" | " | bar | 1.3897 | 1.3225 | 1.1731 | 1.0763 | 1.0311 | 1.0354 | 1.0143 | 1.0064 | 0.98759
outlet density | ρ₃ = P₃ / (R * T₃~) | kg/m³ | 1.7262 | 1.6469 | 1.4536 | 1.3345 | 1.2791 | 1.2776 | 1.2111 | 1.2035 | 1.1792
outlet air speed | u₃ = ṁ / (ρ₃ * A₃) | m/s | 62.2848 | 73.4479 | 49.1575 | 53.5431 | 55.8643 | 10.0542 | 0.16334 | 30.5323 | 0
outlet temperature, final | T₃ = T₂ + (u₂² - u₃²) / (2 * cₚ) | K | 280.5294 | 279.773 | 281.2324 | 281.0062 | 280.8784 | 282.3814 | 291.8077 | 291.3437 | 291.8077
Energy balance checks
energy flowing in at entrance | Ė₁ = ṁ * (cₚ * T₁ + u₁² / 2) | W | 269547.5168 | 269545.1402 | 269542.1063 | 269521.1374 | 269518.944 | 269517.5945 | 269517.5443 | 278464.8321 | 278464.8146
energy flow out downstream | Ė₂ = ṁ * (cₚ * T₂ + u₂² / 2) | W | 269544.9251 | 269542.8602 | 269520.8784 | 269518.944 | 269517.5945 | 269517.5443 | 278464.8321 | 278464.8321 | 278464.7584
energy flow delta (this stage) | ΔĖ = Ė₂ - Ė₁ | W | -2.5917 | -2.2801 | -21.2278 | -2.1934 | -1.3495 | -0.050248 | 8947.2878 | 0 | -0.056214
system energy balance error | Ė_err = (Ė₂ - ΣQᵢ) - Ė₁_stage0 | W | -2.5917 | -4.6566 | -26.6384 | -28.5728 | -29.9223 | -29.9725 | -26.5963 | -26.5963 | -26.67
system energy balance error fraction (w.r.t. total energy) | Ė_err_frac = Ė_err / Ė₁_stage0 | - | -0.0009615% | -0.001728% | -0.009883% | -0.0106% | -0.0111% | -0.01112% | -0.009867% | -0.009867% | -0.009894%
system energy balance error fraction (w.r.t. total input power) | Ė_err_frac = Ė_err / ΣQᵢ |  | -0.02898% | -0.05207% | -0.2978% | -0.3195% | -0.3346% | -0.3351% | -0.2974% | -0.2974% | -0.2982%
Insulation
is exterior? (fully or partially) | - | boolean | 1 | 1 | 1 | 1 | 0 | 0 | 0 | n/a | 1
min temperature this stage | Tmin = min(T₁, T₂) | K | 279.9958 | 280.3691 | 278.8976 | 281.0062 | 280.8784 | 280.8736 | 282.3814 | - | 291.3259
" | " | °C | 6.8458 | 7.2191 | 5.7476 | 7.8562 | 7.7284 | 7.7236 | 9.2314 | - | 18.1759 | TRUE | <-- Is minimum temperature throughout higher than the supply dewpoint?
air stream temperature relative to the local dewpoint | ΔTd = Tmin - select(Td) | K | -6.1542 | -5.7809 | -7.2524 | -5.1438 | 3.9452 | 3.9405 | 5.4483 | - | 5.1759
temperature difference needing insulation | ΔTinsul = abs(min(0, ΔT_insul)) | K | 6.1542 | 5.7809 | 7.2524 | 5.1438 | 0 | 0 | 0 | - | 0
temperature diff from a condensating surface to local ambient | ΔTcond2amb = select(Tamb) - select(Td) | K | 7 | 7 | 7 | 7 | 14.8746 | 14.8746 | 14.8746 | - | 7
iterative thickness calc intermediate value | λ = k * ΔTinsul / (h_insul * ΔTcond2amb) | mm | 3.5167 | 3.3033 | 4.1442 | 2.9393 | 0 | 0 | 0 | - | 0
insulation minimum outside diameter (neglects pipe wall) | Dmin_insul = 2 * λ / ln(D_insul / D) | mm | 156.6656 | 126.4597 | 107.838 | 60.6391 | 23 | 23.23 | 11.6279 | - | 52.3741 | <-- done in units of mm so that iterative solver tols are similar as used for pressure calc iteration
insulation minimum thickness (no margin) | tmin_insul | mm | 28.3328 | 25.7298 | 28.919 | 18.8196 | 0 | 0.115 | 0.057564 | - | 0 | <-- this value has zero margin -- not the design value!
insulation design thickness | t_insul = t_design_factor * tmin_insul | mm | 42.4992 | 38.5947 | 43.3785 | 28.2293 | 0 | 0.1725 | 0.086346 | - | 0
pipe + insulation outer diameter (pipe wall neglected) | D_total_no_wall | mm | 184.9984 | 152.1895 | 136.7569 | 79.4587 | 23 | 23.345 | 11.6855 | - | 52.3741

## borda-carnot derivation
Form of the Borda-Carnot expansion equation I'm deriving as:
Conservation of linear momentum --> ΣF = (ṁ * u)ₒᵤₜ - (ṁ * u)ᵢₙ = ṁ * (u₂ - u₁)
Assume that upstream pressure P₁ acts also upon the downstream area A₂, just past the area change plane.
At a plane just past the area change from A₁ to A₂, we then have:
ΣF = (Force from upstream fluid) + (Force from shoulder wall) - (Force from downstream fluid)
= (P₁ * A₁) + (P₁ * (A₂ - A₁)) - (P₂ * A₂)
= (P₁ - P₂) * A₂
Therefore P₂ = P₁ + ṁ * (u₁ - u₂) / A₂

## alt RSU counts & power
Item | n RSUs per LAS module | n modules per stave or per disk | n staves or disks per assembly | n assemblies | subtotal modules | subtotal RSUs | power (W) | approx # control boards | approx # control boards per assembly
OB L4 | 5 | 16 | 70 | 1 | 1120 | 5600 | 2442.16 | 30.6204 | 30.6204
OB L3 | 6 | 8 | 46 | 1 | 368 | 2208 | 936.376 | 10.061 | 10.061
ED0/HD0 | 5 | 102 | 1 | 2 | 204 | 1020 | 444.822 | 5.5773 | 2.7886
ED1/HD1 | 6 | 258 | 1 | 2 | 516 | 3096 | 1312.962 | 14.1073 | 7.0536
ED2-4/HD2-4 | 6 | 266 | 1 | 6 | 1596 | 9576 | 4061.022 | 43.6341 | 7.2723
|  |  |  | TOTAL | 3804 | 21500 | 9197.342 | 104 | <-- assuming this many and then splitting them proportionally according to # modules
[5 empty] | avg RSUs per module | 5.6519
Description | n RSUs per LAS module | max RSU power per LAS | AncASIC max multiplier | FPC max multiplier | AncASIC max power | FPC max power | total max power per module
- | - | W | - | - | - | - | -
from ref below | 5 | 1.246 | 45% | 30% | 0.5607 | 0.3738 | 2.1805
from ref below | 6 | 1.454 | 45% | 30% | 0.6543 | 0.4362 | 2.5445
averaged by rsu counts | 5.6519 | 1.3229 | 45% | 30% | 0.59531 | 0.39687 | 2.3151
Taken from ePIC Preliminary Design Report - SVT overleaf doc comments in cooling.tex section, 2025-10-22
The numbers there were compiled by Georg.
https://www.overleaf.com/project/67170d690d68308814b3ba47