## Slide 1: Detector Cooling
Girish Gowda
Mechanical Engineer
I^3 Engineering Meeting
March 2nd, 2026

## Slide 2: Heatsink
SS (304) Pipe embedded Aluminum Heatsink.
304 Stainless steel (~16.5 W/mK)
6063 Aluminum (200 W/mk)
Cold Water Feed
Hot Water Return

## Slide 3: Components
1
2
3
4
5
6
8
10
12
13
Number | Name | Power (mW)
1 | DC/DC | 4400
2 | SALSA1 | 1800
3 | SALSA2 | 1800
4 | SALSA3 | 1800
5 | SALSA4 | 1800
6 | LDO_S1 | 450
7 | LDO_S2 | 450
8 | LDO_S3 | 450
9 | LDO_S4 | 450
10 | LDO_lpgbt | 156
11 | LDO_VTRX | 875
12 | lpGBT | 600
13 | VTRX | 175
 | TOTAL | 15,206
7
9
11

## Slide 4: Outer MPGD Detector – Heat Load
Components Heat load data
Component | Power | Power | Area | Area | Heat Flux
 | mW | W | mm^2 | m^2 | W/m^2
DC/DC | 4,400 | 4.4 | 200 | 0.0002 | 22,000
SALSA | 1,800 | 1.8 | 100 | 0.0001 | 18,000
SALSA | 1,800 | 1.8 | 100 | 0.0001 | 18,000
SALSA | 1,800 | 1.8 | 100 | 0.0001 | 18,000
SALSA | 1,800 | 1.8 | 100 | 0.0001 | 18,000
LDO | 450 | 0.45 | 50 | 0.00005 | 9,000
LDO | 450 | 0.45 | 50 | 0.00005 | 9,000
LDO | 450 | 0.45 | 50 | 0.00005 | 9,000
LDO | 450 | 0.45 | 50 | 0.00005 | 9,000
LDO lpGBT | 156 | 0.156 | 50 | 0.00005 | 3,120
LDO VTRX | 875 | 0.875 | 50 | 0.00005 | 17,500
lpGBT | 600 | 0.6 | 100 | 0.0001 | 6,000
VTRX | 175 | 0.175 | 100 | 0.0001 | 1,750
 | 15206 | 15.206 |  |  | 
Inlet
Outlet
Single FEB model

## Slide 5: Outer MPGD Detector – Single FEB Heat Load
FEB | 15.2 | W
with margin | 16 | W
dT | 0.5 | C
Cp | 4181 | J/kg C
m | 0.00741 | kg/s
m | 0.00741 | l/s
m | 7.41 | ml/s
Velocity | 0.467 | m/s
Re | 2198 | Laminar
Temperature rise 0.5 C
Temperature rise 2 C
FEB | 15.2 | W
with margin | 16 | W
dT | 2 | C
Cp | 4181 | J/kg C
m | 0.00185 | kg/s
m | 0.00185 | l/s
m | 1.853 | ml/s
Velocity | 0.1168 | m/s
Re | 549.53 | Laminar
Inlet water Temperature | 22 | C
Ambient Temperature | 23.3 | C

## Slide 6: Results – 0.5C temperature rise, inlet temperature 22C
Temperature distribution

## Slide 7: Results – 2C temperature rise, inlet temperature 22C
Temperature distribution

## Slide 8: Outer MPGD Detector – 7 FEB Heat Load
Number of FEB | 7 | 
Single FEB | 15.5 | W
with margin | 16 | W
Total FEB | 112 | W
dT | 0.5 | C
Cp | 4181 | J/kg C
m | 0.05358 | kg/s
m | 0.05358 | l/s
m | 53.58 | ml/s
Velocity | 3.3761 | m/s
Re | 15883 | Turbulent
Temperature rise 0.5 C
Temperature rise 2 C
Number of FEB | 7 | 
Single FEB | 15.5 | W
with margin | 16 | W
Total FEB | 112 | W
dT | 2 | C
Cp | 4181 | J/kg C
m | 0.01339 | kg/s
m | 0.01339 | l/s
m | 13.39 | ml/s
Velocity | 0.844 | m/s
Re | 3971 | Transition
Inlet water Temperature | 22 | C
Ambient Temperature | 23.3 | C

## Slide 9: 7FEB Model
Inlet
Outlet

## Slide 10: Results – 0.5C temperature rise, inlet temperature 22C
Temperature distribution

## Slide 11: Results – 2C temperature rise, inlet temperature 22C
Temperature distribution

## Slide 12: 7 FEB Heat Load – modified design
Temperature rise 2 C
Number of FEB | 7 | 
Single FEB | 15.5 | W
with margin | 16 | W
Total FEB | 112 | W
dT | 2 | C
Cp | 4181 | J/kg C
m | 0.01339 | kg/s
m | 0.01339 | l/s
m | 13.39 | ml/s
Velocity | 1.392 | m/s
Re | 5145 | Turbulent
Inlet water Temperature | 22 | C
Ambient Temperature | 23.3 | C
Tapered design
Tube ID changed from 4.5 mm to 3.5 mm
OD changed from 5 mm to 4 mm