## Slide 1: BIC Update
Kevin Bailey & Tom O’Connor
Triple I Engineering Meeting Update
June 1, 2026
Power Consumption and Cooling Needs

## Slide 2: Heat Sources in BIC
Astropix Sensors within the sector
End of Sector Box (ESB) – 2 per sector
  End-of Tray Cards (ETC)
  SiPM
  CALOROC Boards

## Slide 3: Heat Sources in BIC
Astropix Sensors within the sector:
2cm by 2cm chips @<2mW/cm2 generates <8mW per chip
218 chips per stave equals 1.7W per stave
4 instrumented trays (6 staves in one and 7 staves in three) with 27 staves total equals 5886 chips and 47W per sector
48 sectors @ 47W per sector equals 2.26kW for the entire barrel

## Slide 4: Heat Sources in BIC
End of Sector Box (ESB) Components:
End-of-Tray Cards (ETC)
  4 ETC per ESB @ 1W/ETC equals 4W per ESB
  2 ESB’s per sector equals 8W per sector
  48 sectors equals 384 W for the entire barrel
SiPM
  60 SiPM per ESB @ 0.2W/SiPM (from GlueX) equals 12W per ESB
  2 ESB’s per sector equals 24W per sector
  48 sectors equals 1.15kW for the entire barrel
CALOROC Boards
  1 board per ESB @ 8W/CALOROC equals 8W per ESB
  2 ESB’s per sector equals 16W per sector
  48 sectors equals 768W for the entire barrel

## Slide 5: Heat Sources in BIC
End of Sector Box (ESB) Components (continued):
ETC + SiPM + CALOROC = 4W + 12W + 8W = 24W per ESB
ESB Totals:
24W per ESP
48W per Sector
2.30kW for the entire barrel

## Slide 6: Heat Sources in BIC
Grand Totals
Astropix + 2xESB= 47W + 48W = 95W per sector
95W per Sector
4.56kW for the entire barrel

## Slide 7: Cooling Strategy
AstroPixsensors: passive cooling strategy
Large total heat load but small heat density and large conductive area radially
Thermal simulations indicate heat evacuation radially outwards through tray walls and through Pb/ScFi layers to 1.25” thick aluminum plate is sufficient
Aluminum plate cooled from the back with room temperature cooling water
End-of-Sector Boxes: active cooling strategy
Higher heat density requires cooling with chilled water loop
Relative temperature stabilization of SiPMs to 7°C in each ESB with thermal mass of 0.5” Aluminum cold plate with embedded cooling loop (5°C water)
Metal-core PCB (1.7 mm) assumed for additional temperature stabilization and homogenization
The ESBs (and hence indirectly the AstorPix layers) will be slow flushed with nitrogen to prevent condensation.