June 23rd, 2026, ePIC safety discussion

Meeting Notes:

- North and South Platforms:

  - Electrically most of the items will be new and will all have to be built to new codes

  - Mechanically were only making small modifications to the platforms so we won’t be re looking at the codes for anything existing

  - Seismic anchoring for North and South platforms will be investigated

    - Have some guidance from external firm

    - Risk assessment of the seismic anchors

- Central Platform:

  - No more equipment racks, the exist sPHENIX platforms will be modified

  - Does the central platform need to follow all of the building and OSHA codes?

    - No, it will be experimental equipment.

  - sPHENIX was built afterwards, meaning that it was lighter when it was moved

  - Detector vs detector, ePIC is ~3.5% heavier but this may not include platforms and racks. So overall the weights may be a wash.

  - Central platform top stairs may be needed for egress, just plan on putting temporary railings and such up top.

- Design Guide Comments:

  - Safety factors look good

  - Be careful about singularities around holes and areas that may be cycling due to the magnet (dynamic loads)

- Code Discussions:

  - Slide 16 Table:

    - All items agreeable

    - Rails should be looked at by Brian’s group as well

    - Lines are drawn at different spots, for example: The platform that holds the cryo equipment is part of building but the cryo equipment is scientific

    - Magnet group’s platforms need to make sure they adhere to OSHA

- General rule of thumb: anything that gets power needs to have about 36” of working space

- Fire protection for the building itself, is any fire suppression or detection needed for the detector or the platforms?

  - Planning to reuse the VESDA system from STAR for ePIC.

  - This includes smoke detectors inside the racks and sniffers inside the detector.

- Eventually include other sections to the design guide. Maybe make separate documents for electrical, fire safety, etc.

- B313 is the code for piping supports

- Detector, experimental hall, assembly hall and tunnel ventilation needs to be looked at

Action Items:

- John will send rack layout to Pat for review.

- Brian will investigate seismic anchoring for the Barrel, Endcaps, and North & South platforms.

  - Mike thinks there likely won’t be a building code requirement for seismic anchors. In that case we should conduct a risk assessment of the seismic anchors for the barrel, endcaps, and platforms.

  - For reference sPHENIX didn’t have anchors.