## Slide 1: sPHENIX Director’s Review
August 2-4, 2017
BNL

## Slide 2: Magnet System Block Diagram

## Slide 3: Magnet Power Supply
Power Supply
  Performance Specifications
    Nominal Magnet Operating Current is 4596 Amps
      PS Max Current 5000 Amps
    Magnet Voltage for ramping is approximately 8 Volts
      PS Max Voltage 20 Volts
    100 ppM Current Regulation
  12 pulse SCR Phase Controlled Power Converter
  Analog PID Current Regulator

## Slide 4: Quench Detector
Quench Detector
  22 Voltage Tap Channels
    4 Dual Gain Channels
  1 Magnet Current Channel
  Two Quench Detector Algorithms for Super-Conducting Coils
    Vmeas – L * di/dt
    Half Coil Comparison
  Fixed Thresholds for Gas-Cooled Leads, Flex Joints, and Super-Conducting Bus
  Front-End Electronics
    Provide isolation to ground of 2500 Vrms
    Provide differential voltage sensing
    Gain appropriate for the channel
    Anti-aliasing filters

## Slide 5: Voltage Tap Locations

## Slide 6: Quench Detector Signal Processing

## Slide 7: Subsystem Collaborators
Zeynep Altinbas BNL
  Quench Detector Software
Winston Pekrul BNL
  Loggers Software
  Strain Gage and Linear Pots Software
  Control System Interface Software
Pablo Rosas BNL
  Power Supply and Energy Extraction Resistor
Carl Schultheiss BNL
  Quench Detector Front-End Electronics
  System Integration

## Slide 8: Schedule Drivers
WBS 1.8.4 Power Supply and Quench Detection Systems
High Field Test
  Power Supply, Energy Dump Resistor, and Quench Detector must all be operational.
  Mid September 2017

## Slide 9: Cost Drivers
Power Supply was provided by SLAC.
  Replaced electrolytic capacitors
  Replaced PLC
Energy Dump Resistor was also provided by SLAC.
  Replaced DC contactor
Power Cables
  $10.00/ft.

## Slide 10: Basis of Estimate and Resource-Loaded Schedule
Basis of Estimate
  Catalog prices
  Engineering Estimates
Resource-Loaded Schedule
  Engineering Estimates
  Experience

## Slide 11: Status and Highlights
Power Supply
  Tested to 2600 Amps .
  Tested with PSI generating ramp.
Quench Detector
  Front-End Electronics Boards in house and under test.
  Quench Detector Software being written.
  Fast and Slow Loggers Software complete.
  Strain Gage Software is complete.