## Sheet1
ePIC SVT Liquid Cooling Flow Stages |  |  | Color key:
Contact: jhsilber@lbl.gov |  |  | INPUT
CALCULATED
Version history |  |  | LINKED
v1 - Aug 18, 2026 - JHS - initial version, with interior parallel channels in cold plate
v2 - Aug 19, 2026 - JHS - cold plate internal channel represented as single, serpentine, rect x-section path, to improve turbulent convection; added total pressure drop check
v3 - Aug 20, 2026 - JHS - cold plate internals represented as fin array
v4 - Aug 21, 2026 - JHS - temp-dependent viscosity and Prandtl #; friction factor fixes; labeling fixes; expansion or contraction handling of outlet pressure
Implementation notes
As of 2026-08-20, not doing any checks whether vena contracta pressure drops to the vapor pressure (cavitation), because dynamic pressures << 0.5 bar of sub-atmospheric supply (i.e. fluid velocities are << √(2P/ρ) = 10 m/s).
Physical constants and unit conversions
density (H₂O) | ρ | kg/m³ | 1000
dynamic viscosity (H₂O) | μ | Pa*s | 0.0010521
specific heat capacity (H₂O) | cₚ | J/(kg*K) | 4184
Prandtl number (H₂O) | Pr | - | 7.3378
thermal conductivity (H₂O) | k | W / (m*K) | 0.6
zero celsius | T₀ | K | 273.15
infinity | ∞ | - | 1e+99
Pa per bar | Pa_per_bar | - | 100000
in H₂0 per bar | inH20_per_bar | - | 401.463
psi per bar | psi_per_bar | - | 14.5038
bar per atm | bar_per_atm | - | 1.0132
Boundary conditions
source temperature | Tₛ | °C | 18 | 291.15 | K | Modified Chilled Water (MCW) from shared supply manifold with other detectors
source mass flow rate | ṁ_src | kg/s | 0.1
source volume flow rate | Vₛ = ṁₛ / ρ | m³/s | 0.0001 | 6 | L/min
allowable max pressure drop | ΔP_avail | Pa | 50000 | 0.5 | bar | Assuming a chiller like Chilldyne CDU 300 with max 0.5 bar differential
Control board heat load and counts
CB power per board | Q_cb | W | 7.1 | 2025-07-10 Glover presentation, https://indico.bnl.gov/event/28216/contributions/109417/attachments/63357/108750/25-07-10_RDO_board_SVT_working_meeting_%20JJG_rev2.pdf
SCB power per board | Q_scb | W | 7.1 | for now, assume similar to CB
total CBs | n_cb = n_cb_per * n_cb_nets | - | 108
total SCBs | n_scb = n_scb_per * n_scb_nets | - | 68
total boards | n_tot = n_cb + n_scb | - | 176
fraction that are CBs | fc = n_cb / n_tot | - | 0.61364
fraction that are SCBs | fs = n_scb / n_tot | - | 0.38636
avg power per board | Q_b = fc*Q_cb + fs*Qscb | W | 7.1
Control board / cold plate geometry
CB cold plate, interior volume width "a" | a_cb | mm | 44 | EC-1016-5993-A.2 (2026-04-03), as received from A. Huddart
CB cold plate, interior volume width "b" | b_cb | mm | 43 | EC-1016-5993-A.2 (2026-04-03), as received from A. Huddart
SCB cold plate, width "a" | a_scb | mm | 16 | guesstimate given EC-1016-5991-A.2, 2026-04-03, placeholder exterior dimensions 150 mm x 20 mm
SCB cold plate, width "b" | b_scb | mm | 100 | guesstimate given EC-1016-5991-A.2, 2026-04-03, placeholder exterior dimensions 150 mm x 20 mm
cold plate interior height | hp | mm | 2.5 | EC-1016-5993-A.2 (2026-04-03), as received from A. Huddart
cold plate height gap from ceiling to tops of fins | hg | mm | 0.1
cold plate fin height | hf | mm | 2.4 | 0.0024 | m
cold plate fin thickness | tf | mm | 0.4 | 0.0004 | m
cold plate gap between fins | gf | mm | 0.8 | 0.0008 | m
num fins within CB cold plate | nf_cb = a_cb / (tf + gf) | - | 36.6667
num fins within SCB cold plate | nf_scb = a_scb / (tf + gf) | - | 13.3333
typ num fins within generic cold plate | nf = fc * nf_cb + fs * nf_scb | - | 27.6515
typ flow length within generic cold plate | Lp = fc * b_cb + fs * b_scb | mm | 65.0227
cold plate flow perimeter | Xp = 2 * nf * (tf + gf + hf) + 2 * hp | mm | 204.0909
cold plate flow cross-sectional area | Ap = hf * (nf * gf) + (hp - hf) * nf * (gf + tf) | mm² | 56.4091 | 5.6409e-05 | m²
fins total surface area | Af = nf * (2 * hf + tf) * Lp | mm² | 9349.48 | 0.0093495 | m²
cold plate inner walls surface area | Ap_surf = Xp * Lp | mm² | 13270.5475 | 0.013271 | m²
cold plate hydraulic inner diameter | Dp = 4 * Ap / Xp | mm | 1.1056
Collections of individual boards into local serial coolant networks
num CBs per serial network | n_cb_per | - | 9
num SCBs per serial network | n_scb_per | - | 17
num CB serial networks | n_cb_nets | - | 12 | 3 x (hadron + e-) x (top + bottom)
num SCB serial networks | n_scb_nets | - | 4 | 2 x (top + bottom)
num total serial networks | n_nets_tot = n_cb_nets + n_scb_nets | - | 16
avg num control boards per serial network | nc = (n_cb + n_scb) / n_nets_tot | - | 11
typical length between cold plates within a serial network | L_net_int | mm | 100 | approximated from inspection of EC-1016-5993-A.2 (2026-04-03)
Control board / cold plate heat transfer check
cold plate fin thermal conductivity | kf | W/(m*K) | 167 | aluminum 6061-T6
fin array form drag factor | K_fd | - | 4 | typically in the range 2.0 - 4.0, depending on fin array details
cold plate fin parameter | mf = √(2 * h / (kf * tf)) | 1/m | 266.1662
cold plate fin efficiency | ef = tanh(mf * (hf + tf/2)) / (mf*(hf+tf/2)) | - | 0.86598
mass flow rate through cold plate | ṁ_p = mass flow of a given serial network below | kg/s | 0.00625
Reynold's number through cold plate | Re = same as internal channel calcs below | - | 116.4316
flow type | see below | - | laminar
friction factor | see below | - | 0.54968
Nusselt number through cold plate | Nu = 4.36 (laminar) or (f/8) * (Re-1000) * Pr / (1 + 12.7*(f/8)^0.5 * (Pr^(2/3)-1)), transitional, Gnielinski, or 0.023 * Re^0.8 * Pr^0.4 (turbulent, Dittus-Boelter) | - | 4.36
convection coefficient through cold plate | h = Nu * k / D_ch | W/(m² * K) | 2366.2047
convection-limited conductance w.r.t. fluid temperature | H_convec = h * ((Ap_surf - Af) + ef * Af) | W/K | 28.4359
thermodynamically-limited max heat transport | H_capacity = ṁ_p * cₚ | W/K | 26.15
number of transfer units | NTU = H_convec / H_capacity | - | 1.0874 | to avoid being convection-limited, would like this value in the neighborhood of 1 or higher
cold plate effectiveness | ε = 1 - exp(-NTU) | - | 0.66291
fluid temp rise of single plate in series network | ΔTfs = ΔTf / nc | °C | 0.27156
hottest cold plate wall temperature | T = ΔTfs *(1/ε - 1) + T₂ | °C | 21.1262
Tees, elbows, fittings, etc
approx num misc tees, elbows, fittings, etc per stage | nₓ | - | 3
form-drag factor per item for misc losses | Kₓ_per | - | 1 | typical range 0.5-1.5 per item
form-drag factor per stage for misc losses | Kₓ = nₓ * Kₓ_per | - | 3
Each "stage" consists first of a length of pipe with a friction factor, then a change of cross-sectional area
1 = entrance = at beginning of stage
2 = downstream = after pipe length, but before area change
3 = outlet = manifold = after area change
stage description | - | - | from supply manifold to hadron + electron sides | exterior branches to top + bottom halves | interior branches to CB and SCB networks | CB and SCB boards / cold plate internal channels | CB and SCB network pipes (between cold plates) | interior return lines from CB and SCB networks | exterior top&bottom half return manifolds to hadron&electron side return manifolds | from hadron + electron sides back to source
stage index | - | - | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
num channels (per parent channel) | nᵢ | - | 2 | 2 | 4 | 1 | 1 | 1 | 0.25 | 0.5 | <-- values > 1 are splits, less than 1 are mergers
total num parallel channels in system | Nᵢ = product(nᵢ) | - | 2 | 4 | 16 | 16 | 16 | 16 | 4 | 2
mass flow per channel | ṁ = (ṁ_src or previous stage ṁ) / nᵢ | kg/s | 0.05 | 0.025 | 0.00625 | 0.00625 | 0.00625 | 0.00625 | 0.025 | 0.05 | 0.1 | kg [check-product], mass flow is split exactly among branches at each stage, i.e. assuming each branch has similar back-pressure
num identical elements in series within this channel | nₛ | - | 1 | 1 | 1 | 11 | 10 | 1 | 1 | 1
length | L | m | 10 | 15 | 7 | 0.065023 | 0.1 | 7 | 15 | 10
hydraulic diameter (mm) | D_mm | mm | 19 | 19 | 5 | 1.1056 | 3.6 | 5 | 19 | 19
hydraulic diameter | D | m | 0.019 | 0.019 | 0.005 | 0.0011056 | 0.0036 | 0.005 | 0.019 | 0.019
" | " | inches | 0.74803 | 0.74803 | 0.19685 | 0.043526 | 0.14173 | 0.19685 | 0.74803 | 0.74803
single channel cross-sectional area along length L | A₁₂ = π D² / 4 (circular cross-section) or as calculated elsewhere for non-circular | m² | 0.00028353 | 0.00028353 | 1.9635e-05 | 5.6409e-05 | 1.0179e-05 | 1.9635e-05 | 0.00028353 | 0.00028353
all channels total cross-sectional area | ΣA₁₂ = A₁₂,ᵢ * Nᵢ | m² | 0.00056706 | 0.0011341 | 0.00031416 | 0.00090255 | 0.00016286 | 0.00031416 | 0.0011341 | 0.00056706
" | " | cm² | 5.6706 | 11.3411 | 3.1416 | 9.0255 | 1.6286 | 3.1416 | 11.3411 | 5.6706
entrance temperature | T₁ = Tₛ or previous stage T₃ | K | 291.15 | 291.1501 | 291.1501 | 291.1509 | 294.1381 | 294.1386 | 294.1394 | 294.1394
Reynold's number | Re = ṁ * D / (A₁₂ * μ) | - | 3184.7923 | 1592.3961 | 1512.7763 | 116.4316 | 2101.0782 | 1512.7763 | 1592.3961 | 3184.7923
flow type | define laminar @ Re <= 2300 and turbulent @ 4000 | - | transitional | laminar | laminar | laminar | laminar | laminar | laminar | transitional
friction factor (laminar, Hagen-Poiseuille) | f_lam = 64/Re = 0.316/Re^0.25 otherwise | - | 0.020096 | 0.040191 | 0.042306 | 0.54968 | 0.030461 | 0.042306 | 0.040191 | 0.020096
friction factor (turbulent, Blasius) | f_turb = 0.3164 / Re^0.25 | - | 0.042118 | 0.050087 | 0.050733 | 0.096321 | 0.046733 | 0.050733 | 0.050087 | 0.042118
friction factor (selected) | f = f_lam or f_turb | - | 0.042118 | 0.040191 | 0.042306 | 0.54968 | 0.030461 | 0.042306 | 0.040191 | 0.042118
form-drag factor | K_fd | - | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0
friction pressure drop (Darcy-Weisbach) | ΔP₁₂ = (f * (L/D) + K_fd + Kₓ/nₛ) * ṁ² / (2 ρ A₁₂²) * nₛ | Pa | 391.3382 | 135.0073 | 3152.5503 | 2471.2861 | 2160.5921 | 3152.5503 | 135.0073 | 391.3382
" | " | bar | 0.0039134 | 0.0013501 | 0.031526 | 0.024713 | 0.021606 | 0.031526 | 0.0013501 | 0.0039134
" | " | psi | 0.056759 | 0.019581 | 0.45724 | 0.35843 | 0.31337 | 0.45724 | 0.019581 | 0.056759
power input to stream | Qᵢ = Q_per_serial_element * nₛ | W | 0 | 0 | 0 | 78.1 | 0 | 0 | 0 | 0
total applied power (all parallel and serial elements) | ΣQᵢ = Qᵢ * Nᵢ | W | 0 | 0 | 0 | 1249.6 | 0 | 0 | 0 | 0 | <-- note total applied power, and cross-check to other top-down estimates
volumetric flow rate | V = ṁ / ρ | m³/s | 5e-05 | 2.5e-05 | 6.25e-06 | 6.25e-06 | 6.25e-06 | 6.25e-06 | 2.5e-05 | 5e-05
flow speed | u = V / A₁₂ | m/s | 0.17635 | 0.088174 | 0.31831 | 0.1108 | 0.61402 | 0.31831 | 0.088174 | 0.17635
friction heating of fluid | Qf = ΔP₁₂ * V | W | 0.019567 | 0.0033752 | 0.019703 | 0.015446 | 0.013504 | 0.019703 | 0.0033752 | 0.019567
fluid temperature rise | ΔTf = (Qᵢ + Qf) / (ṁ * cₚ) | K | 9.3532e-05 | 3.2268e-05 | 0.00075348 | 2.9872 | 0.00051639 | 0.00075348 | 3.2268e-05 | 9.3532e-05
downstream temperature | T₂ = T₁ + ΔTf | K | 291.1501 | 291.1501 | 291.1509 | 294.1381 | 294.1386 | 294.1394 | 294.1394 | 294.1395
" | " | °C | 18.0001 | 18.0001 | 18.0009 | 20.9881 | 20.9886 | 20.9894 | 20.9894 | 20.9895
cross-sectional area on other side of outlet | A₃ = next stage's (A₁₂ * nᵢ) | m² | 0.00056706 | 7.854e-05 | 5.6409e-05 | 1.0179e-05 | 5.6409e-05 | 7.0882e-05 | 0.00014176 | 1e+99
area change pressure drop at outlet (expansion case) | ΔP₂₃_exp = nₛ * ṁ²/(2*ρ) * (1 - A₁₂/A₃)²/A₁₂², where A₃ > A₁₂ | Pa | 3.8874 | 26.4812 | 21.5306 | 1392.8 | 1266.1818 | 26.4812 | 3.8874 | 15.5495 | Borda-Carnot expansion loss
area change pressure drop at outlet (contraction case) | ΔP₂₃_con = nₛ * ṁ²/(2*ρ) * (1 - A₃/A₁₂)/A₃² * 0.42, where A₁₂ > A₃ | Pa | -1.6327 | 15.3834 | -4.8283 | 713.7731 | -117.0882 | -4.2613 | 3.2654 | 0 | empirical contraction loss (vena contracta)
area change pressure drop at outlet | ΔP₂₃ = ΔP₂₃_exp or ΔP₂₃_con | Pa | 3.8874 | 15.3834 | 21.5306 | 713.7731 | 1266.1818 | 26.4812 | 3.2654 | 15.5495
friction + outlet pressure drop for this stage | ΔPᵢ = ΔP₁₂ + ΔP₂₃ | Pa | 395.2256 | 150.3908 | 3174.0809 | 3185.0591 | 3426.7739 | 3179.0314 | 138.2727 | 406.8877
total pressure drop | ΔPtot = cumulative Σ ΔPᵢ | Pa | 395.2256 | 545.6164 | 3719.6973 | 6904.7564 | 10331.5304 | 13510.5618 | 13648.8345 | 14055.7223 | 3.5573 | <-- check whether sufficiently low pressure loss? ΔP_avail / ΔP_tot must be comfortably larger than 1.0
" | " | bar | 0.0039523 | 0.0054562 | 0.037197 | 0.069048 | 0.10332 | 0.13511 | 0.13649 | 0.14056
" | " | psi | 0.057323 | 0.079135 | 0.5395 | 1.0015 | 1.4985 | 1.9595 | 1.9796 | 2.0386

## H2O props
Temp. [°C] | Dyn. Viscosity [mPa.s] | polynomial check | polynomial error | Kin. Viscosity [mm²/s] | Density [g/cm³] | Polynomial
2 | 1.6735 | 1.6667 | -0.4046% | 1.6736 | 0.9999 | -0.056598 | 0.0011096 | -1.1955e-05 | 5.2009e-08 | 1.7756
3 | 1.619 | 1.6155 | -0.2189% | 1.6191 | 1
4 | 1.5673 | 1.5662 | -0.07068% | 1.5674 | 1
5 | 1.5182 | 1.5189 | 0.04419% | 1.5182 | 1
6 | 1.4715 | 1.4734 | 0.1309% | 1.4716 | 0.9999
7 | 1.4271 | 1.4298 | 0.1886% | 1.4272 | 0.9999
8 | 1.3847 | 1.3879 | 0.2315% | 1.3849 | 0.9999
9 | 1.3444 | 1.3477 | 0.2459% | 1.3447 | 0.9998
10 | 1.3059 | 1.3091 | 0.2473% | 1.3063 | 0.9997
11 | 1.2692 | 1.2721 | 0.2299% | 1.2696 | 0.9996
12 | 1.234 | 1.2366 | 0.2116% | 1.2347 | 0.9995
13 | 1.2005 | 1.2026 | 0.1711% | 1.2012 | 0.9994
14 | 1.1683 | 1.1699 | 0.136% | 1.1692 | 0.9992
15 | 1.1375 | 1.1386 | 0.09327% | 1.1386 | 0.9991
16 | 1.1081 | 1.1085 | 0.03762% | 1.1092 | 0.9989
17 | 1.0798 | 1.0797 | -0.008868% | 1.0811 | 0.9988
18 | 1.0526 | 1.0521 | -0.05017% | 1.0541 | 0.9986
19 | 1.0266 | 1.0256 | -0.1003% | 1.0282 | 0.9984
20 | 1.0016 | 1.0001 | -0.1448% | 1.0034 | 0.9982
21 | 0.9775 | 0.97576 | -0.1776% | 0.9795 | 0.998
22 | 0.9544 | 0.95237 | -0.2131% | 0.9565 | 0.9978
23 | 0.9321 | 0.92991 | -0.2348% | 0.9344 | 0.9975
24 | 0.9107 | 0.90836 | -0.2573% | 0.9131 | 0.9973
25 | 0.89 | 0.88766 | -0.263% | 0.8926 | 0.997
26 | 0.8701 | 0.86778 | -0.2668% | 0.8729 | 0.9968
27 | 0.8509 | 0.84867 | -0.2617% | 0.8539 | 0.9965
28 | 0.8324 | 0.83031 | -0.2516% | 0.8355 | 0.9962
29 | 0.8145 | 0.81264 | -0.2285% | 0.8178 | 0.9959
30 | 0.7972 | 0.79564 | -0.1962% | 0.8007 | 0.9956
31 | 0.7805 | 0.77926 | -0.1587% | 0.7842 | 0.9953
32 | 0.7644 | 0.76348 | -0.12% | 0.7682 | 0.995
33 | 0.7488 | 0.74827 | -0.07118% | 0.7528 | 0.9947
34 | 0.7337 | 0.73358 | -0.01591% | 0.7379 | 0.9944
35 | 0.7191 | 0.7194 | 0.04192% | 0.7234 | 0.994
36 | 0.705 | 0.70569 | 0.09829% | 0.7095 | 0.9937
37 | 0.6913 | 0.69243 | 0.1635% | 0.6959 | 0.9933
38 | 0.678 | 0.67959 | 0.2341% | 0.6828 | 0.993
39 | 0.6652 | 0.66714 | 0.2915% | 0.6702 | 0.9926
40 | 0.6527 | 0.65506 | 0.3619% | 0.6579 | 0.9922
45 | 0.5958 | 0.5995 | 0.6214% | 0.6017 | 0.9902
50 | 0.5465 | 0.55039 | 0.7113% | 0.5531 | 0.988
55 | 0.5036 | 0.50616 | 0.5086% | 0.5109 | 0.9857
60 | 0.466 | 0.46605 | 0.01073% | 0.474 | 0.9832
65 | 0.4329 | 0.43006 | -0.6564% | 0.4415 | 0.9806
70 | 0.4035 | 0.39897 | -1.122% | 0.4127 | 0.9778
75 | 0.3774 | 0.37436 | -0.8062% | 0.3872 | 0.9748
80 | 0.354 | 0.35856 | 1.288% | 0.3643 | 0.9718
Source: | https://wiki.anton-paar.com/en/water/

## outer barrel cb counts (for ref
Item | n modules per stave or per disk | n staves or disks per assembly | n assemblies | subtotal modules | approx # control boards | approx # control boards per assembly
OB L4 | 16 | 70 | 1 | 1120 | 30.6204 | 30.6204
OB L3 | 8 | 46 | 1 | 368 | 10.061 | 10.061
ED0/HD0 | 102 | 1 | 2 | 204 | 5.5773 | 2.7886
ED1/HD1 | 258 | 1 | 2 | 516 | 14.1073 | 7.0536
ED2-4/HD2-4 | 266 | 1 | 6 | 1596 | 43.6341 | 7.2723
|  |  | TOTAL | 3804 | 104 | <-- assuming this many and then splitting them proportionally according to # modules