## Slide 1: Environmental Controls
1002 F Laser Building
Past – Present – Future
RHIC Tunnel @ 1002
Brian Streckenbach

## Slide 2: Definitions and FYI’s
Ton – unit of cooling capacity
  12,000 BTU/H
    ~3500 watts
  HVAC unit
HVAC companies
  Bard
  Mitsubishi
  Trane/Carrier
Laser Trailer nomenclature
  Broken into two rooms
    Laser Room (proper)
    Foyer/ Anteroom
DX – Direct expansion
  Or known as a split unit
Direct Digital Controls - DDC
  Automated Logic Corporation (ALC – BNL Standard)
    Building automation
Notes: Amount of Energy to melt 1 Ton of ice in 24 hours @ 32 degrees

## Slide 3: Laser Building HVAC Layout - Original
Notes: Defines the Cooling distribution.

## Slide 4: General Overview of HVAC controls (Laser Trailer)
5 Ton Bard unit (past)
  Original Design
    Based on original Environmental conditions
3 Ton Bard unit (Laser room) and a 2 Ton Mitsubishi unit (Anteroom) (Present)
  Due to Change in heat load conditions
3 Ton Bard with Variable capacity (Future)
Separate Humidity control
  Proposed 2018 Changes
    Response to request for increase stability
ALC controls with ductwork modifications and HVAC overhaul.
  Proposed 2019+ changes
    Extensive invasive rework required; too disruptive to commissioning program

## Slide 5: LEReC Laser Parameters
Parameters, and changes to Room | Temperature Regulation | Humidity Regulation | AC System Implemented
Original configuration (CeC laser only) | +/- 1 degree | 50% +/- 5 | Bard 5 Ton
Added Lasers and Chillers, Heat load in Foyer Increased | +/- 0.5 degree (winter) +/- 1 degree (summer) | 40% +/- 10% | Bard 3 Ton / Mitsubishi 2 Ton
Decouple Dehumidification from AC unit | +/- 0.5 degree (winter) +/- 1 degree (summer) | 40% +/- 5% | Added in Separate Dehumidifier
Change AC input from step input to Ramp input | +/- 0.5 degree (no 20min Cycle) | 40% +/-5% (no 20min. Cycle) | Change to Variable Capacity Bard Unit
Dedicated HVAC system with ALC control (if needed) | +/- 0.5 degree | 40% +/-2.5% | New DX unit with ALC controls
Good
Bad
Somewhere in between
Notes: Conditions where we are

## Slide 6: Original HVAC System
5 Ton cooling
  4 Tons in Laser room
  1 Ton in the Anteroom
6KW reheat section
Condition Changed
Issues that arose
  Too much heat load in Anteroom from Chillers
    Excessive temperature excursions in Anteroom and Laser room
    Anteroom saw temperatures of 100 Degree F

## Slide 7
June 2017
5 Ton bard unit
(Laser room)

## Slide 8: Foyer
Large temperature Rise

## Slide 9: Initial Proposed Fix
Separate Cooling for Laser room and Anteroom
  3 Ton Bard unit
  2 Ton Mitsubishi
Bard 3 Ton
Mitsubishi 2 Ton

## Slide 10
August 2018
3 Ton Bard
Results
Notes: Greater temperature stability in anteroom and Laser room
20 Minute temperature and humidity swing cycle
Short Cycling of AC unit (Bard unit)
  Due to how Bard unit functions and low load conditions in winter

## Slide 11: Foyer
Mitsubishi 2 Ton – after install

## Slide 12: Current Changes
Place Dehumidifiers in laser room to further reduce humidity and increase environmental stability
  Larger Floor unit in place now (as shown)
    Replace with two wall mount up-flow units (for redundancy)
Replace the 3 Ton Bard unit with an equivalent footprint Bard unit – Variable Capacity
  Variable Capacity units are terrible for Humidity control
  Great for temperature stability
  20% - 100% capacity
    Reduce short cycling
    Further increase humidity stability
Lead time for Proposed work
  Delivery to BNL on Tuesday November 20th
  Work completed by Friday November 23rd
    Electricians
    Insulation shops
    Sheet metal shops
    AC shop
Notes: Decoupled the Bard unit Humidistat, and humidity coil

## Slide 13
September 2018
Added Dehumidifier
Results
Notes: Increased environmental stability
  With temperature/ humidity upset
    Upsets are on a small scale
  Temperature anomalies do not affect system

## Slide 14: Future upgrade: Variable Capacity
Variable Capacity Bard Unit
  3 Ton unit – with ramp function input
  Flatten out Temperature and Humidity
Trane/ Carrier system with new duct work
  DX system for just the laser room
  Ductwork to laser room only
    Keep Mitsubishi unit
  ALC control system for laser to achieve greater room stability

## Slide 15: 1002 Tunnel HVAC
2017 repair of AC units feeding the IR
  General AC stability for 1002 IR is considered good

## Slide 16: Summary
Tighter equipment requirements and new laser equipment caused original HVAC system obsolescence.
Variable Capacity bard unit will provide better environmental stability
Bard units used for more stringent requirements may not be adequate – DX/ALC alternative (backup) work plan
Notes: DX ALC package in back pocket