## Slide 1: sPHENIX Director’s Review SC MAGNET POWER SUPPLY AND CONTROLS
Carl Schultheiss
April 9-11, 2019
BNL

## Slide 2: WBS 2.02.04
Magnet PS/Controls/Quench Protection
SC Magnet Power Supply
Energy Dump Resistor
Quench Detector
Controls

## Slide 3: sPhenix Magnet System

## Slide 4: sPhenix Power Supply
Power Supply
  Output 20V @ 5000 Amps
  Input 480 Vac @ 200 Amps
  12 Pulse Star Configuration
  Free-Wheeling Diodes
  Water Cooled

## Slide 5: Energy Dump Resistor
2 Contactors 6000 Amps
Water Cooled Bus
Local Controls
Local Status
Relay Logic

## Slide 6: sPhenix Voltage Taps

## Slide 7: Quench Detector System

## Slide 8: QD System Front End
Copy RHIC Quench Detector Front End
Voltage Clamp
  Designed for 300 V, exponential decay with a time constant of 39.5 seconds. (L/R = 2.57 H / 65 mOhm)
Open Lead Detection
Isolation
Gains
  Gain of 10 for superconducting busses
  Gain of 1 for magnet coils, gas-cooled leads, flex bus

## Slide 9: Quench Detector
22 Voltage Tap Channels
5 Aux Input Channels
  Magnet Current
  PS Current
  PS Voltage
  Ground Current
  Dump Resistor Voltage

## Slide 10: sPhenix PS Control Page

## Slide 11: Schedule Drivers
Power Supply and Energy Dump Resistor moved to 1008B.
  Not in final position, depends on the final design of water-cooled bus.
  Quench Detector rack will be in 1008B, near the power supply.
New Quench Detector Calculation Engine is under design.
  Prototype planned by 2021.

## Slide 12: Cost Drivers
Water-cooled Bus
Cable Tray
Electrical Distribution
Quench Detector Calculation Engine

## Slide 13: High Field Test Results
Completed the High Field Test.
  Operated magnet at 4830 Amps
  105% of operational current (4596 Amps).
  Proved Quench Detector Operation
    Established quench limits, 50 mV
    Tested quench interlocks
      Fast Discharge
      Slow Discharge
  Measured Inductances, Inner 1.081 H, Outer 1.112 H
  Measured Gas-Cooled Leads’ flow-rate requirement
  0.32 g/sec at 105%.

## Slide 14: High Field Test Results
Notes: 2.0 Amps/sec to 2000 Amps
1.5 Amps/sec to 4830 Amps
Slow Discharge took 1 hour

## Slide 15: Issues and Concerns
New Quench Detector Calculation Engine.
  NI system was not fast enough to do all the calculations we wanted.
  Make the sPhenix Quench Detector a satellite of the new RHIC QD.
  Working on prototype, it should be ready 2021.
Voltage Taps VT10 and VT11
  VT11 opened during cooldown
  VT10 opened during at 2800 Amps on 2/9/2018
  Rerouting wiring to connector at bottom of chimney
  Opened up “Old Doghouse” to repair VT11 and add redundant taps.

## Slide 16: New Doghouse SC Junction