## Slide 1: Crab cavities cryogenics – constraints and solutions
Crab Cavity review – Brookhaven National Laboratory, USA
5-6 May 2014
K. Brodzinski
on behalf of cryogenic team at CERN

## Slide 2: Contents
Cryogenics for SPS
  Cryogenic circuits
  Heat load and cooling capacity discussion – new heavy constrain
Cryostat design
  Cryostat circuits and instrumentation
  SM-CM interface first concept
  Pressures, protection and safety, operation aspects
Cryogenics for LHC - concept for LHC P1 and P5
Conclusions

## Slide 3: Cryogenic infrastructure in SPS BA4
CC x 2
black –> existing 4.5 K
red –> to be constructed 2 K
Crab cavity cooling at 2 K  TCF20 cryoplant used in pure liquefaction
TCF20 means 20 l/h = 0.7 g/s of LHe, expected max.1.5 g/s with LN2 boost
TCF20 T-S Diagram
Guaranteed capacity in refrigeration mode: 87.5 W @ 4.5 K
(i.e. isentropic equivalent to ~0.85 g/s of liquefaction)
The cold box is OK and will run for COLDEX until end of 2015 but has not sufficient capacity for CC testing in liquefaction mode !

## Slide 4: Consequence
CC x 2
Service module
Coupler/HOM/LOM intercept
CWT
CWT
Screen
Screen
R
LT
TT
PT
JT
EH
TT
black –> existing 4.5 K
red –> to be constructed 2 K
Regarding 2 K refrigeration
CC cryostat
EH
Buffer tank
From LN2
precooler
Draft version
Second source of LHe

## Slide 5: Heat load 1/2
5
Equipment | Heat load | Source of capacity
Service module | ~2.5 W @ 4.5/2K ~30 W @ 80 K | Cold box -> 0.13 g/s LN2
Buffer tank | ~1.5 W @ 4.5 K | Cold box -> 0.08 g/s
Transfer lines | ~4 W @ 4.5 K | Cold box -> 0.21 g/s
Cryo module static | ~14 W @ 2 K 223 W @ 80 K | Cold box -> 0.68 g/s LN2
Cryo module dynamic | ~11 W @ 2K | Buffer -> 0.5 g/s
Total static: | ~22 W | Cold box -> ~1.1 g/s
R. Bonomi, O. Capatina, F. Carra, V. Parma, K. Brodzinski
CC Annual review, CERN, December 2013
Equipment | Heat load | Source of capacity
Service module | ~2.5 W @ 4.5/2K ~30 W @ 80 K | Cold box -> 0.13 g/s LN2
Buffer tank | ~1.5 W @ 4.5 K | Cold box -> 0.08 g/s
Transfer lines | ~4 W @ 4.5 K | Cold box -> 0.21 g/s
Cryo module static | ~18.6 W @ 2 K 286 W @ 80 K | Cold box -> 0.9 g/s LN2
Cryo module dynamic | ~13.4 W @ 2K ~30 W @ 80 K | Buffer -> 0.6 g/s LN2
Total static: | ~26.6 W | Cold box -> ~1.32 g/s
Current estimation
1.32*1.5=1.98 g/s
0.6*1.5=0.9 g/s

## Slide 6: Consequence
CC x 2
Service module
Coupler/HOM/LOM intercept
CWT
CWT
Screen
Screen
R
LT
TT
PT
JT
EH
TT
black –> existing 4.5 K
red –> to be constructed 2 K
Regarding 2 K refrigeration
CC cryostat
EH
Buffer tank
From LN2
precooler
Draft version
Second source of LHe
The cryogenics is to be upgraded to higher capacity – it will cost money and time

## Slide 7: Solutions for BA4 cryo capacity
7
BA4
TCF20
max. ~1.5 g/s with boost
storage
TCF20’ CNRS CB
max. 2.1 g/s (for indication: 0.12 g/s -> 150 L buffer filling time of ~40 h)
BA4
storage
TCF200 (w/o comp.)
max. 7 g/s
CryoLab
TCF50
max. ~3 g/s with boost
1:
Comments:
Additional time needed to remove old CB and install new one or add new one to the installation
Still well limited with the new CB in case of replacement, potential problems with integration and handling of flush from the buffer in case of new CB adding
Comments:
Additional time needed to remove old CB and install new one
CryoLab affected with availability and additional work, new compressor for TCF200 is to be bought
Both options require additional money, manpower and time to perform the mechanical work at BA4 after end of COLDEX operation and before CC SPS testing (~min. 1 month – to be precisely calculated).
2:
State of the Art is required for the cryo module design.

## Slide 8: Heat load 2/2
8
Summary (assuming cold box capacity of 3 g/s):
Total Static: 1.98 g/s
Dynamic: 0.9 g/s
Total Static + Dynamic = 1.98+0.9=~2.9 g/s < 3 g/s -> run without buffer is theoretically possible
For security reasons we plan to install 150 L dewar for dynamic heat load compensation
The aim is to design the system in a such a way to provide cooling capacity for at least 8 hours of operation /day (refilling of the dewar will be done during the nights).

## Slide 9: Process and instrumentation
Draft version - still some discussions are needed with module builders to match with the final design

## Slide 10: Safety devices
Assembly of cavity with helium tank have to be designed to withstand pressure of at least 2.6 bar (deltaP of 2.6 bar) without plastic deformation at ambient temperature.
Design pressure for the cryostat assembly should be based on installed safety devices according to design rules (cryostat equipped with a safety valve set at 1.8 bara* and a rupture disc set at 2.2 bara*, possibly one device could be installed … - analysis underway)
both safety devices will be installed in the way to avoid potential projection of helium towards the passages or transport areas (deflectors installation to be analyzed, preliminary position for the rupture disc and safety valve have been proposed on transfer line close to the cryostat interface),
Both safety devices should protect the cavity and the cryostat from pressure rise causing plastic deformations,
Both safety devices should be equipped with appropriate helium guards.
sizing of the devices -> to be done
helium tank
crab cavity
common pumping collector
thermal screen at ~80 K
cryostat interface
CWT
Power coupler intercept
CWT
SKETCH
Rupture disc @ 2.2 bara
SV @ 1.8 bara
* Value compatible with recommendations given by T. Peterson on December 2012 Fermilab meeting

## Slide 11: Pumping collector sizing
87
Requirements: gas speed lower than 5 m/s*, min 50 mm for level regulation, additional buffer for ~ 20 min of operation, compatibility with safety devices for pressure limit requirements.
Indications: Diameter of 100 mm (recommended) allows for:
return gas speed below 5 m/s up to ~90 mm of liquid level in the collector (operation regulation level to be set at ~50 mm of LHe in the collector),
buffer volume for transients/unexpected process perturbations (half filled collector allows for ~15-20 min of operation assuming collector length of ~1.6 m and 30 W of thermal load),
compatibility with safety valves sizing is still to be checked !
* Calculation done assuming: collector diameter of 100 mm, He mass flow = 3 g/s, GHe temp = 2 K, GHe press = 20 mbar.
100 mm
~87 mm
0 mm
Liquid level
~50 mm
Regulation
maxi: 5 m/s
* Value compatible with recommendations given by T. Peterson on December 2012 Fermilab meeting

## Slide 12: SM to CM interface 1/2
ID100
DN200
304x3.2
ID10
ID10
ID15
30
45
75
66
66

## Slide 13: SM to CM interface 2/2
Concept of Service Module to Cryo Module jumper connection
CM
SM
310
330
380
304
~530
The internal lines will be equipped with flexible hoses on SM side,
the connection concept study is underway, 3D model with necessary dimensions should be ready by end of June.
vacuum
ambient

## Slide 14: 2 K helium pumps
The check shows that assuming inlet pressure of 20 mbar two pumping units are capable to pump ~2.3 g/s of helium, what gives ~3.5 g/s at 30 mbar (2 K saturation)
OK for CC SPS test

## Slide 15: 2 K helium pumps installation at BA4
The 2 K helium pumps have been installed in the SPS cavern at BA4 end of April 2014.
The related utilities connection will follow and will be operational by end of June 2014.

## Slide 16
16
Pressures – safety :
The cavity should be designed to withstand external pressure of 2.6 bara (deltaP = 2.6 bar) at ambient temperature without plastic deformation,
Design pressure for the cryostat should be based on installed safety devices according to design rules (cryostat equipped with a rupture disc set at 2.2 bara and safety valve set at 1.8 bara)
  both safety devices should be placed on the cryostat in the way to avoid potential projection of helium towards the passages or transport area (deflectors installation to be analyzed),
  Both safety devices should protect cavity and cryostat from pressure rise causing plastic deformations
Operating pressure during the cool down can oscillate between 1.2 and 1.5 bara – estimation,
Normal operation pressure will be set at ~ 30 mbara (for 2 K cooling)
Cryostat operation – first approach
Cool down – stable operation – warm up:
Cool down will be done with direct filling of LHe to the cavity cryostat, roughly estimated cool down time is ~ 1 day
Stable operation availability can be affected by impurities in the system or unexpected utilities cut.
Warm up of the cavities will be done by evaporation of helium and warm gas circulation

## Slide 17: New cryogenic infrastructure at P1 and P5
1 warm compressor station (WCS) in noise insulated surface building
1 upper cold box (UCB) in surface building
1 cold quench buffer (QV) in surface
1 or 2 cold compressor boxes (CCB) in underground cavern
2 main cryogenic distribution lines
2 interconnection valve boxes with existing QRL
L. Tavian_Daresbury 2013
Suitable for cryogenics to have a common cryostat for 2 or 4 CC in one module. Supply and pumping lines architecture is being studied -> it will result in number of jumpers (consideration of tunnel slope is mandatory).

## Slide 18: Conclusions
The existing BA4 cryogenics has to be upgraded to higher cooling capacity – additional money, manpower and time will have to be allocated – study on SPS unavailability during the work has to be studied, replacement is to be done after COLDEX run is completed,
Service Module to CC Cryo Module interface design is underway – to be defined with 3D model by end of June 2014,
2 K pumping units – capacity test done -> 2 units transported and installed in SPS,
Remaining components of the infrastructure are to be ordered and built until end of 2015,
Cryogenic safety and risk analysis has to be done for SPS BA4 prior to operation,
Close collaboration with regular working sessions is needed to merge between CERN requirements and the modules suppliers.
Thank you! Questions?