## Slide 1: Variable Voltage Substation Fire
John Seabury, Accelerator Directorate Quality and Safety Manager
5 August, 2014
DOE Accelerator Safety Workshop
Unofficial!

## Slide 2: Background
Original SLAC 3 km electron Linac was constructed in the mid-1960’s
  Based upon 30, 100-m sectors, each of which has 8 klystrons (except at injectors) providng RF power to the accelerator
Mid-2000’s Sectors 21-30 were separated from Sectors 0-20
  Sectors 21-30 got a new injector and provide electrons to the Linac Coherent Light Source (LCLS)
  Sectors 0-20 provide electrons to Facility for Advanced Accelerator Experimental Tests (FACET)
    In 2016 the “guts” of Sectors 0-10 will be demolished and the space repurposed as LCLS-II (new cryogenic accelerator modules)
    Sectors 11-20 are under discussion for additional experiments
    Sectors 21-30 will remain as LCLS
  Linac klystron AC power distribution system is essentially unchanged since the 1960’s

## Slide 3: AC Power Distribution to Linac Klystrons
250 kV pulse
250 kV pulse
Master Substation (A/B)
12.47 kV switchgear
transformer
600 V switchgear
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
60 kV
12.47 kV
Sector (typ of 30)
Sector (typ of 30)
Variable Voltage Substation
(typ of 15)
300-600 V
230 kV

## Slide 4: 12.47 kV Power Distribution to VVS Subs
VVS 15
VVS 14
VVS 13
VVS 12
VVS 11
VVS 10
VVS 9
VVS 8
VVS 7
VVS 6
VVS 5
VVS 4
VVS 3
VVS 2
VVS 1B
VVS 1A
Master Substation
62
40
36
VV1
VV2
VV3
76
VV4
61
VV5
64
VV6
30
VV7
LCLS
FACET
Linac

## Slide 5: Incident Response and Initial Assessment
  6/25 Wednesday
    2145 VVS13 tripped. Vesda system alarmed. Onsite electrician reported that VVS13 was on fire.
      Second alarm, 22 apparatus from sheriff and local fire departments responded
      So did news crews from three local television stations
    2225 12kV locked off, suppression commences. EOC activated, notifications made.
    2300 fire is out
    2345 PPS is interrupted, locked out
    Linac East (Sectors 0-20)
  6/26 Thursday
    ~0200 EOC deactivated
    News report went viral
    During day: assess damage to 12kV
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 6: AC Power Distribution to Linac Klystrons
250 kV pulse
250 kV pulse
Master Substation (A/B)
12.47 kV switchgear
transformer
600 V switchgear
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Modulator
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
Klystron
60 kV
12.47 kV
Sector (typ of 30)
Sector (typ of 30)
Variable Voltage Substation
(typ of 15)
300-600 V
230 kV
6/25 Fire
VVS13

## Slide 7: 12.47 kV Power Distribution to VVS Subs
VVS 15
VVS 14
VVS 13
VVS 12
VVS 11
VVS 10
VVS 9
VVS 8
VVS 7
VVS 6
VVS 5
VVS 4
VVS 3
VVS 2
VVS 1B
VVS 1A
Master Substation
62
40
36
VV1
VV2
VV3
76
VV4
61
VV5
64
VV6
30
VV7
LCLS
FACET
Linac

## Slide 8: Recovery
  6/27 Friday
    Inspect other VVS on affected 12 kV legs, PPS bypass VVS13
      Problems found with four of five other VVS, repairs made
    Restored 12kV ~1700, modulators ~2200
  6/28 Saturday
    Early am, LCLS and FACET user beams restored (LCLS at reduced power) ~50 hours user interruption
  6/29 Sunday
    Beam tuning continues, experiments in progress
  6/30 Monday
    Accepted subcontractor bid. Suspected asbestos in arc chutes, sampled debris
    News of fire had become yesterday’s news, little further interest
  7/1 Tuesday
    Asbestos confirmed, abatement crew brought in, begin prep of VVS4
  7/4 Friday
    Abatement completed, began installation of replacement VVS
  7/9 Wednesday
    VVS13 on line, full LCLS power restored, ~14 days recovery
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 9: VVS13 Repair - Replacement Project
…containment
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 10: VVS13 Repair - Replacement Project
…containment
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 11: VVS13 Repair - Replacement Project
…abatement complete, clearance received, containment removed, VVS removed.
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 12: VVS13 Repair - Replacement Project
…VVS4 riding down the gallery
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 13: VVS13 Repair - Replacement Project
…VVS4 at its new home in S26
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 14: VVS13 Repair - Replacement Project
…new modulator conductors readied for pull
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 15: VVS13 Repair - Replacement Project
…complete!!!
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum

## Slide 16: Where do we go from here?
  Investigation is underway, report with recommendations is being prepared
  August/September downtime includes detailed inspection and maintenance on all VVS
  Right now we have no spare VVS
    We do have designs and could have additional ones fabricated, but that likely would be weeks offline
    After 2016 there will be spare VVS available from the demolition of Sectors 0-10 for LCLS-II
Notes: Outline scope of work (won’t change often)
Highlight any scoping decisions or changes
Keep drawings and photos to a minimum