## Slide 1
Geoff Savage
09-Jan-2020
ICARUS DAQ Racks to pORC

## Slide 2: Outline
Tasks needed to complete the installation of the ICARUS DAQ racks
  pORC – partial Operational Readiness Clearance
What are we talking about?
  Physical location of DAQ racks at SBN-FD
  DAQ rack layouts
Computing summary
  All DAQ racks installed in final locations
  Right now computers are powered directly from the wall to the PDU
    No rack protection
  Computers are fully networked
  All computers have operating systems installed
Rack types – each type has different requirements
  TPC (x4)
  PMT (x1) and CRT top
  CRT side and bottom (x2)
  Central Servers/EVB/Timing
  Clk/DCS (x1)
pORC documentation needs to be written

## Slide 3: DAQ Rack Locations at SBN-FD
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
EB
X
DAQ fiber drop
X
X
Alcove 1
Mezz W
Alcove 2
Mezz W

## Slide 4: Alcove 1 Mezzanine West – Central Servers/EVB/Timing
RPS | 1 | RPS | 1 |  |  | 44 |  |  |  | 
space | 2 | space | 2 |  |  | 43 |  |  |  | 
 |  |  |  | RPS | 1 | 42 | RPS |  |  | RPS
AC Switch Box-30 | 2 | AC Switch Box-30 | 2 | space | 1 | 41 | space |  |  | space
 |  |  |  | AC Switch Box-30 | 2 | 40 | AC Switch Box-30 |  |  | AC Switch Box-30
space | 1 | space | 1 |  |  | 39 |  |  |  | 
 |  |  |  | space | 1 | 38 | space |  |  | space
 |  |  |  | icarus-gateway01 | 1 | 37 | s-sbn-fd-daq-1 (10Gb) | rear |  | 
 |  |  |  | space | 1 | 36 | cables |  |  | 
 |  |  |  | icarus-gateway02 | 1 | 35 | s-sbn-fd-dcs-2 (1Gb) | rear |  | 
 |  |  |  | space | 1 | 34 | cables |  |  | 
 |  |  |  | icarus-db01 | 2 | 33 |  |  |  | 
 |  |  |  |  |  | 32 |  |  |  | 
 |  |  |  | space | 1 | 31 |  |  |  | 
 |  |  |  | icarus-db02 | 2 | 30 |  |  |  | 
 |  |  |  |  |  | 29 |  |  |  | 
 |  |  |  | space | 1 | 28 |  |  |  | 
 |  |  |  | icarus-nfs01 | 2 | 27 |  |  |  | 
 |  |  |  |  |  | 26 |  |  |  | 
 |  |  |  | space | 1 | 25 |  |  |  | 
 |  |  |  | icarus-nfs02 | 2 | 24 |  |  |  | 
 |  |  |  |  |  | 23 |  |  |  | 
 |  |  |  | space | 2 | 22 |  |  |  | 
 |  |  |  |  |  | 21 | management server |  |  | icarus-clk01
 |  |  |  | KVM | 1 | 20 | space |  |  | space
 |  |  |  | space |  | 19 | icarus-evb01 |  |  | icarus-clk02
 |  |  |  |  |  | 18 |  |  |  | space
 |  |  |  |  |  | 17 | space |  |  | icarus-dcs01
 |  |  |  |  |  | 16 | icarus-evb02 |  |  | 
 |  |  |  |  |  | 15 |  |  |  | 
 |  |  |  |  |  | 14 | space |  |  | 
 |  |  |  |  |  | 13 | icarus-evb03 |  |  | 
 |  |  |  |  |  | 12 |  |  |  | 
 |  |  |  |  |  | 11 | space |  |  | 
 |  |  |  |  | 21 | 10 | icarus-evb04 |  |  | 
 |  |  |  |  |  | 9 |  |  |  | 
 |  |  |  |  |  | 8 | space |  |  | 
 |  |  |  |  |  | 7 | icarus-evb05 |  |  | 
 |  |  |  |  |  | 6 |  |  |  | 
 |  |  |  |  |  | 5 | space |  |  | 
 |  |  |  |  |  | 4 | icarus-evb06 |  |  | 
 |  |  |  |  |  | 3 |  |  |  | 
 |  |  |  |  |  | 2 | space |  |  | 
 |  |  |  |  |  | 1 |  |  |  | 
EVB
Timing
CS

## Slide 5: Alcove 2 Mezzanine West – TPC/CRT/PMT
 |  |  |  |  |  | 47 |  |  |  |  | RPS | 47 | RPS |  | RPS
 |  |  |  |  |  | 46 |  |  |  |  | space | 46 | space |  | space
 |  |  |  |  |  | 45 |  |  |  |  | AC Switch Box-30 | 45 | AC Switch Box-30 |  | AC Switch Box-30
RPS |  | RPS |  | RPS |  | 44 | RPS |  |  |  |  | 44 |  |  | 
space |  | space |  | space |  | 43 | space |  |  |  | space | 43 | space |  | space
 |  |  |  |  |  | 42 |  |  |  |  | s-sbn-fd-dcs-5 | 42 | s-sbn-fd-daq-3 (10Gb) | rear | s-sbn-fd-dcs-6
AC Switch Box-30 |  | AC Switch Box-30 |  | AC Switch Box-30 |  | 41 | AC Switch Box-30 |  |  |  | cables | 41 | cables |  | cables
 |  |  |  |  |  | 40 |  |  |  |  |  | 40 |  |  | 
space |  | space |  | space |  | 39 | space |  |  |  |  | 39 |  |  | 
s-sbn-fd-dcs-3 (1Gb) | rear | fiber distribution |  | s-sbn-fd-daq-2 (10Gb) | rear | 38 | s-sbn-fd-dcs-4 |  |  |  |  | 38 |  |  | 
cables |  | cables |  | cables |  | 37 | cables |  |  |  |  | 37 |  |  | 
 |  |  |  |  |  | 36 |  |  |  |  |  | 36 |  |  | 
 |  |  |  |  |  | 35 |  |  |  |  |  | 35 |  |  | 
 |  |  |  |  |  | 34 |  |  |  |  |  | 34 |  |  | 
 |  |  |  |  |  | 33 |  |  |  |  |  | 33 |  |  | 
 |  |  |  |  |  | 32 |  |  |  |  |  | 32 |  |  | 
 |  |  |  |  |  | 31 |  |  |  |  |  | 31 |  |  | 
 |  |  |  |  |  | 30 |  |  |  |  |  | 30 |  |  | 
 |  |  |  |  |  | 29 |  |  |  |  |  | 29 |  |  | 
 |  |  |  |  |  | 28 |  |  |  |  |  | 28 |  |  | 
 |  |  |  |  |  | 27 |  |  |  |  |  | 27 |  |  | 
 |  |  |  |  |  | 26 |  |  |  |  |  | 26 |  |  | 
 |  |  |  |  |  | 25 |  |  |  |  |  | 25 |  |  | 
 |  |  |  |  |  | 24 |  |  |  |  |  | 24 |  |  | 
 |  |  |  |  |  | 23 |  |  |  |  |  | 23 |  |  | 
 |  |  |  |  |  | 22 |  |  |  |  |  | 22 |  |  | 
icarus-tpc19 |  | icarus-tpc13 |  | icarus-tpc07 |  | 21 | icarus-tpc01 |  |  |  |  | 21 |  |  | icarus-pmt01
 |  |  |  |  |  | 20 |  |  |  |  | icarus-crt09 | 20 | icarus-crt01 |  | 
space |  | space |  | space |  | 19 | space |  |  |  | space | 19 | space |  | space
icarus-tpc20 |  | icarus-tpc14 |  | icarus-tpc08 |  | 18 | icarus-tpc02 |  |  |  | icarus-crt10 | 18 | icarus-crt02 |  | icarus-pmt02
 |  |  |  |  |  | 17 |  |  |  |  | space | 17 | space |  | 
space |  | space |  | space |  | 16 | space |  |  |  | icarus-crt11 | 16 | icarus-crt03 |  | space
icarus-tpc21 |  | icarus-tpc15 |  | icarus-tpc09 |  | 15 | icarus-tpc03 |  |  |  | space | 15 | space |  | icarus-pmt03
 |  |  |  |  |  | 14 |  |  |  |  |  | 14 | icarus-crt04 |  | 
space |  | space |  | space |  | 13 | space |  |  |  |  | 13 | space |  | space
icarus-tpc22 |  | icarus-tpc16 |  | icarus-tpc10 |  | 12 | icarus-tpc04 |  |  |  |  | 12 | icarus-crt05 |  | icarus-pmt04
 |  |  |  |  |  | 11 |  |  |  |  |  | 11 | space |  | 
space |  | space |  | space |  | 10 | space |  |  |  |  | 10 | icarus-crt06 |  | space
icarus-tpc23 |  | icarus-tpc17 |  | icarus-tpc11 |  | 9 | icarus-tpc05 |  |  |  |  | 9 | space |  | icarus-pmt05
 |  |  |  |  |  | 8 |  |  |  |  |  | 8 | icarus-crt07 |  | 
space |  | space |  | space |  | 7 | space |  |  |  |  | 7 | space |  | space
icarus-tpc24 |  | icarus-tpc18 |  | icarus-tpc12 |  | 6 | icarus-tpc06 |  |  |  |  | 6 | icarus-crt08 |  | icarus-pmt06
 |  |  |  |  |  | 5 |  |  |  |  |  | 5 |  |  | 
space |  | space |  | space |  | 4 | space |  |  |  |  | 4 |  |  | space
icarus-tpc25 |  | icarus-tpc26 |  | icarus-tpc27 |  | 3 | icarus-tpc28 |  |  |  |  | 3 |  |  | icarus-pmt07
 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  | 
space |  | space |  | space |  | 1 | space |  |  |  |  | 1 |  |  | space
TPC2
TPC1
TPC3
TPC4
CRT2
CRT1
PMT

## Slide 6: Common Computing Rack Items
Rack protection
  AC switch box, rack protection system, and smoke detector
    Items are at FD
    Power cords from AC switch box to wall and AC switch box to PDU need to be routed
    No holes to mount smoke detectors in computing racks
  Is this really needed for DAQ racks with all commercial equipment?
  Cover fronts and backs?
Power cords
  Right now the cords are pulling down and exposing ground prongs on plug
    Skippy suggested flipping the PDU upside down so the two prongs are on top and the ground prong is on the bottom
  Labels for power cords are in a spreadsheet which needs to be updated if there are PDU adjustments, then printed and affixed
Grounding - PDUs
Network cables
  All network cables are installed but not labeled
  Labels for network cables are in a spreadsheet which needs to be printed and the labels affixed

## Slide 7: Requirements by rack type
TPC (x4)
  Common computing rack items
  Trunk fibers and fiber pigtails to PCIe cards
    Need a horizontal surface to store excess
    Routing to PCIe cards
PMT (x1)
  Common computing rack items
  DAQ fibers
    Probably need a horizontal surface to store excess
    These DAQ fibers are sturdier than the TPC DAQ fibers
CRT (x2)
  Common computing rack items
  DAQ cat5 cables
Central Servers/EVB/Timing
  Common computing rack items
  Timing rack would have RG-174 connections if a SPEC card is installed in clk02 computer.
Clk/DCS
  Common computing rack items

## Slide 8: TPC3 Rear

## Slide 9: Network Connections
EVB
TPC/PMT
CRT
Key:
Yellow – DAQ Cat6a
Yellow/Green tape – Public Cat6a
Blue – IPMI
Green – Public
Green/Red tape - DCS

## Slide 10: Comments from Linda Bagby
Regarding the rack protection question:
  The decision for rack protection is typically up to the collaboration.
  I suggest rack protection.
  You may want to talk to an experiment that decided against it (Nova).
  (The result of their experience is why I changed to a smoke sensor model that includes temperature.)
Regarding power plug blade exposure:
  This is usually due to the weight of the cable.
  Strain relief and cable twist orientation works wonders.

## Slide 11: Moving Forward
Decide if rack protection is needed
  If rack protection is used then the power cord length from the rack to the wall needs to be determined for the power cords to be made.
Rack protection will be installed
  Let Bill know the power cord lengths so they can be put together
Identify solutions to the other open issues
  Routing of DAQ fibers
  Power cord
Implement solutions
Attach network cable labels
  Labels have been printed
  Verify connections using link lights
Label power cords
  Decide on layout in racks
  Make label spreadsheet
  Attach labels
pORC documentation

## Slide 12: Installation Requirements
At least two people to meet the ODH 1 requirement
Installation will take about 6 weeks of calendar time
  Arrive at Fermilab – badge, training (ODH)
  Installation is an iterative process
    Discuss and refine installation tasks
    Locate tools and parts
    Perform installation
    Review installation
  Write documentation
  pORC walk through
  Resolve issues from pORC walk through
Usually people coming to work at Fermilab also have other responsibilities that they can’t ignore and must spend time on
The ORC process for ICARUS for cabling and racks is directed and guided by Linda Bagby as the Electrical working group leader. The cabling must meet Fermilab standards. I am not aware of all the standards and consult with Linda as the task progresses.

## Slide 13: Installing Rack Protection
Rack protection has three units
  AC switch box – cuts power when smoke/over temperature is sensed
  Rack protection system – Triggers power cut via AC switch box
  Smoke/temperature detector -
  Cables and power cords
Installation
  Install the three units
  Connect cables and power cords
  Rack will need to be powered off when connecting the AC switch box to the wall power
Parts and Tools
  M6 cage nuts and bolts
  Screw drivers
  Make some hanger parts for the smoke detectors because of the lack of holes in the top of the computing rack
Rack protection needs to be installed in 9 of the 10 DAQ racks

## Slide 14: Rack Protection w/ Smoke detector

## Slide 15: RPS and AC Switch Box in Rack (Front)

## Slide 16: RPS and AC Switch Box in Rack (Back)

## Slide 17: Installing Power Cords
Power cords are plugged into a vertical Power Distribution Unit (PDU) in each rack
Right now the cords are pulling down and exposing ground prongs on the plug
One suggestion is to flip the PDU upside down so the two prongs are on top and the ground prong is on the bottom
We need to consult with others to determine the best way to resolve this item
I recommend flipping the PDU in one rack and see if the plugs hold better
Labels for power cords are in a spreadsheet which needs to be updated if there are PDU adjustments, then printed, and affixed
This applies to all 10 DAQ racks

## Slide 18: Installing Networking
All network cables have been connected
Labels need to be attached to each end
61 computers x 4 labels/computer x 2 ends = 488 labels
Verify the connections
  Disconnect one end and verify the link lights go off on both ends.
  Need to organize a time when the DAQ is not used to do this
Labels have been printed

## Slide 19: Installing DAQ Fibers
TPC DAQ fibers
  The DAQ fibers consist of three sections
    Trunk cables with 24 fibers in one cable
    Then on each end there are pigtails
    Pigtails transition from the trunk fiber to individual fibers
  Status
    Trunk fibers are in place
    Pigtails on the detector top will be installed next week (I think)
  Pigtails in the TPC racks need to be installed horizontally
    Shelves have been installed in the TPC and PMT racks for horizontal installation
    Every individual fiber in the pigtail needs a label (already printed)
    24 computers x 16 fibers/computer = 384 labels
PMT DAQ fibers
  Status
    Fibers are in place across the detector
    Aiwu connected fibers to the DAQ computers
    Right now the fibers are vertical, probably want them horizontal
  Need to think about the positioning
  Label these fibers if they are not labeled yet
Parts and Tools
  Tie wraps
  Scissors
  Inner duct
There are four TPC racks and one PMT rack

## Slide 20: Installing CRT Racks
The bottom and side CRT groups need to run networking cables between the readout and computers in their two DAQ racks.
  They would probably accept help to get the cables managed in their two racks
I have no information on the top CRT.